## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2021-07-08
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: https://sunspec.org/sunspec-specifications/
Copyright SunSpec Alliance 2009-2021. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4040 Moorpark Avenue Suite 110
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Implementation
Sunspec Identification
Device Modbus maps begin at one of three Modbus base addresses.
Preferred Base Register: 40001
Alternate Base Register: 50001
Alternate Base Register: 00001
All SunSpec device maps begin at one of the base addresses and start with the 32-bit ‘SunS’ identifier (0x53756e53).
This allows for discovery of SunSpec compatible devices.
If the base register does not return this value, the alternate base registers are checked.
Model Identification
After the start address, the sunspec model mapping will start at X0002 (ex : 40002).
Each sunspec model will at first provides their ID and their Lenght.
All sunspec model are put ones after anothers in the modbus addresses.
This allows the easy discovery of sunspec models.
The End of SunSpec Map is represented with the value 0xFFFF
Best Practice
As Sunspec is in a continuous developpement, model are not fixed and can be extend in the futur.
For that reason, automatic scanning of Sunspec model is the best practice to communicate with another system.
You can also implement only the needed data by reading only the needed registers.
By doing manual mapping, you expose your system to communication incompatibility in case of update on our system.
For all the reasons explain above, Socomec encourage you to use automatic scan in order to developped your EMS communication with our system.
Socomec will not be responsible for system unavaibility after a software upgrade if you have made manual mapping.
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter (superseded by the 700 series)
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | DER
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is programmatically generated from SunSpec model definition files, which can be downloaded from:
https://github.com/sunspec/models
Please note that the SunSpec model definition files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at:
https://sunspec.org/sunspec-specifications/
SunSpec Certification
If you would like to have your product SunSpec Certified you can apply for Certification here:
https://sunspec.org/sunspec-certification-application/
After applying, someone from SunSpec will followup shortly.
You can also contact certification@sunspec.org to ask questions and start the process.

## Change Log
Date | Issue # | Models | Change
02-03-23 (SOCOMEC version 3.2.2.0 based on SunSpec "v29-09-22")
Update columns order
16-01-23 (SOCOMEC version 3.2.1.0 based on SunSpec "v29-09-22")
|  | 64901 | Update Alarm A027 Update Warning W026
|  | 702 | Set as not used : VMaxRtg ; VMinRtg ; AMaxRtg ; ReactSusceptRtg ; S_SF
|  | 703 | Set as not used : ESRndTms
|  | 703 | Set as used : ESRmpTms ; ESDlyRemTms ; V_SF ; Hz_SF
|  | 705 | Set as used : ID ; L ; Pri ; Vref ; VRefAuto ; VRefAutoEna ; VRefAutoTms ; RspTms ; ReadOnly
|  | 706 | Set as used : ID ; L ; RspTms
|  | 715 | Set as used OpCt
|  | 802 | Set as used : EvtVnd1 ; EvtVnd2 ; CellVMax ; CellVMin
|  | 803 | Set as used : ID ; L ; SoH_SF
20-10-22 (SOCOMEC version 3.2.0.0 based on SunSpec "v29-09-22")
|  | 64901 | Add of W027, W029, W058, W059, W060, W062, W063, W076, W077, W087, W088, W089, W090
|  | 64901 | Add of A015, A028, A096, A098, A099, A112, A113
|  | 64901 | Update description W019,021,023,052,055,056 and A021,022,029
|  | 64901 | Update Label W021 and A030.
|  | 64901 | Rework A009, A011, A026, A093.
29-09-22 (SOCOMEC version 3.1.0.0 based on SunSpec "v2021-07-08")
|  | 64901 | Add of A003 - SoC out of range for Off-Grid alarm
|  | 64901 | Correct State Word 2
|  | 64901 | Update description of W012, W013, W026, W086, A027
26-09-22 (SOCOMEC version 3.1.0.0 based on SunSpec "v2021-07-08")
|  | 64901 | Add of A003 - SoC out of range for Off-Grid alarm
21-01-22 (SOCOMEC version based on SunSpec "v2021-07-08")
|  | 64902 | Vendor model 64902 added
10-08-21 (SOCOMEC version based on SunSpec "v2021-07-08")
|  | 64901 | Vendor model 64901 added
07-08-21
| 221 | 704, 705 | Removed Power Priority enums IEEE_1547, PF
| 224 | 704 | To point VarSetMod added enum VA_MAX_PCT
06-01-21
|  | 701 | Changed all power factor points to signed
|  | 701 | For point InvSt changed symbol "MPPT" to "RUNNING"
10-05-21 (SOCOMEC version based on SunSpec "v2021-04-20")
| - | 713 | Add model 713, shift address of 715 and 802
| - | All models | Green cells are implemented in PMS
04-23-21
|  | 713 | Updated Model Length
04-16-21
|  | 713 | Added SF 'Pct_SF', assigned SF to points SoC, SoH
|  | 711 | Fixed labels and descriptions
04-15-21
|  | 700 series | Updated labels and descriptions. Fixed typos.
|  | 700 series | Removed notes attribute.
06-04-21 (SOCOMEC version based on SunSpec "v2021-03-02")
| - | All models | Green cells are implemented in PMS
03-02-21
| 197 |  | Updated JSON schema
| 201 | 705-712 | Made ReadOnly point Mandatory and Static
| 198 | All models | Added size to all points in all models. Size is now mandatory.
|  | All models | Updated JSON schema to make "size" required on point object
| 199 | 701-715 | Made ID, L, and Ena point labels consistent
| 162 |  | Added symbols to point schema
| 205 | 705-712 | Fixed labels on Ena point
| 200 | 711 | Added point 'PMin'
| 34 | 803 | Changed point 'ModTmpAvg' type to 'int16'
01-21-21
| 195 | 702 | Made all read-only points Static
| 194 | 1 | Made all points except DA Static
| 193 | 704 | Changed point naming 'xxxRvrtEna' to 'xxxEnaRvrt'
| 181 | 802 | Fixed description for point 'SoCRsvMin'
| 192 | 16 | Changed 'Ctl' point type to 'bitfield16'
01-13-21
| 190 | 705 | Model 705; For points 'VRef', 'VRefAuto' added sf 'V_SF' and units 'VRefPct'
01-12-21
| 187 | 715 | Fixed incorrect model length
01-11-21
| 184 | All 700 | All enums now use 0 based indexing
| 163 | 715 | Update points 'DERHb', 'ControllerHb' type to uint32
| 185, 180 | 701, 702, 703, 704, 713, 715 | Added model lengths
| 179 | 701 | Fixed typo
12-14-20
| 177 | 714 | Updated point 'DCSt' to 'DCSta'
| 176 | 713 | Added point 'St'
| 175 | 701, 702 | Fixed numbering on symbols for points 'ThrottSrc' and 'CtrlModes'
| 174 | 704 | Added point 'AntiIslEna'
| 173 | 713 | Reordered points
12-04-20
| 171 | 701 | Changed point 'ACType' to Mandatory
12-03-20
| 158 | 707-710 | Fixed typo in description
| 159 | 712 | Changed point 'Pri' access to 'RW'
| 164 | 701 | Changed points with units 'V' to type 'uint16'
| 165 | 703 | Added point 'ESDlyRemTms'
| 166 | 701 | Removed symbols from point St, added point DERMode
| 167 | All 700 | Capitalized word 'id' in labels and descriptions
| 168 | 713, 714, 715 | Created new 713, incremented old 713, 714
11-05-20
| 154 | 704, 705, 706, 712 | Changed point type to int16 for points: (704) 'WSetPct', 'WSetPctRvrt', 'VarSetPct', 'VarSetPctRvrt'; (705) 'Var'; (706) 'W'; (712) 'W', 'Var'
| 155 | 701 | Added point 'InvSt'
| 153 | 701 | Removed notes
| 156 | 714 | Added model 714
10-30-20
| 141 | 701, 703, 704, 705, 706, 709, 710, 711, 712 | Update to make Point type and units consistent across models
| 119 | 702 | Add symbols to points 'IntIslandCatRtg', 'IntIslandCat
| 151 | 702 | Adds points 'PFOvrExt' and 'PFUndExt'
| 150 | 704 | Changed point names 'RGra' -> 'WRmp' and 'RGraRef' -> 'WRmpRef
| 147 | 704 | Add 'Pct' to 'WMaxLim' points, updated labels
| 149 | 705, 712 | Add symbol 'VA_MAX_PCT' to point 'DeptRef'
| 150 | 704 | Add point 'VarRmp'
| 144 | 702 | Update point 'Vnom' to 'VNom'
| 146 | 701 | Update PF points type to uint16
| 148 | 701 | Change point 'VL3N' to 'VL3'
| 145 | 705-712 | Remove CrvSt point
| 142 | 711 | Adds label to 'Ena' point
| 139 | 702 | Changed point 'IntIslandCatRtg' access to ReadOnly
| 134 | 707, 708, 709, 710 | Tms point type changed to uint32, Freq point renamed to Hz
| 130 | 705, 706 | Added RspTms_SF point
| 124 | 705 | Changed point name 'VRefTms' to 'VRefAutoTms'
09-17-20
| 131 | 712 | Changed 'W' point type to 'int16'
|  | All 700 series | Capitalized labels
| 129 | 711 | Added ReadOnly point to Controls
| 127 | 706 | fixed incorrect description for 'W' point
| 125 | 701 | Changed 'Hz' point type to uint32
| 122 | 705 | Changed Pri point to RW
| 121 | 704 | Set VarSetPri to RW
| 117 | 711 | Changed point names to use control naming
| 115 | 701 | Changed abbreviation of "Manufacturer" to "Mn"
| 116 | 704 | changed all reversion enables to read-write
09-03-20
| 112 | 705 | added VRefAutoEna and updated VRefAuto
| 110 | 702 | changed symbol names for the CtrlModes point to use '_TRIP' instead of 'RT'
| 113 | 702 | Removed VRefOfs point
| 114 | 702 | Reordered the order of the settings points to match the order of the ratings points
Updated schema.json to include the "notes" property
| 109 |  | Removed Detail Description, replaced with Notes
08-03-20
| 101 | 713 | Added symbols to the DCSt point
| 107 | 704 | Fix reversion enable functionality
| 102 | 704 | added RGraRef point
| 96 | 101 | fixed wrong sf name for points: TotVarhInj and TotVarhAbs
| 103 | 713 | fixed Tmp point detail description typo
| 100 | 707 | fixed NCrvSet misspelling
06-03-20
| 89 | 707, 708, 709, 710 | Added ReadOnly point to Crv group with access set to R
| 94 | 707, 708, 709, 710 | Changed curve points access to RW
| 93 | 705, 706, 707, 708, 709, 710, 712 | Changed curve points mandatory to optional
| 95 | 703 | Changed L access to R
| 92 | 705 | Changed VRefAuto type to enum16, added DISABLED 0 as enumeration
| 91 | 707, 708, 709, 710 | Added enumeration values for CrvSt
| 90 | 705, 706 | Changed ReadOnly access to R
| 88 | 707, 708, 709, 710 | Changed ActPt access to RW
| 87 | 707, 708, 709, 710 | Changed name of NCrv to NCrvSet

## Index
HEX Address | DEC Address | Model | Label | Description
9C42 | 40002 | 1 | Common | All SunSpec compliant devices must include this as the first model
|  | 2 | Basic Aggregator | Aggregates a collection of models for a given model id
|  | 3 | Secure Dataset Read Request | Request a digital signature over a specified set of data registers
|  | 4 | Secure Dataset Read Response | Compute a digital signature over a specified set of data registers
|  | 5 | Secure Write Request | Include a digital signature along with the control data
|  | 6 | Secure Write Sequential Request | Include a digital signature along with the control data
|  | 7 | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response
|  | 8 | Get Device Security Certificate | Security model for PKI
|  | 9 | Set Operator Security Certificate | Security model for PKI
|  | 10 | Communication Interface Header | To be included first for a complete interface description
|  | 11 | Ethernet Link Layer | Include to support a wired ethernet port
|  | 12 | IPv4 | Include to support an IPv4 protocol stack on this interface
|  | 13 | IPv6 | Include to support an IPv6 protocol stack on this interface
|  | 14 | Proxy Server | Include this block to allow for a proxy server
|  | 15 | Interface Counters Model | Interface counters
|  | 16 | Simple IP Network | Include this model for a simple IPv4 network stack
|  | 17 | Serial Interface | Include this model for serial interface configuration support
|  | 18 | Cellular Link | Include this model to support a cellular interface link
|  | 19 | PPP Link | Include this model to configure a Point-to-Point Protocol link
|  | 101 | Inverter (Single Phase) | Include this model for single phase inverter monitoring
|  | 102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
|  | 103 | Inverter (Three Phase) | Include this model for three phase inverter monitoring
|  | 111 | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
|  | 112 | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
|  | 113 | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
|  | 120 | Nameplate | Inverter Controls Nameplate Ratings
|  | 121 | Basic Settings | Inverter Controls Basic Settings
|  | 122 | Measurements_Status | Inverter Controls Extended Measurements and Status
|  | 123 | Immediate Controls | Immediate Inverter Controls
|  | 124 | Storage | Basic Storage Controls
|  | 125 | Pricing | Pricing Signal
|  | 126 | Static Volt-VAR | Static Volt-VAR Arrays
|  | 127 | Freq-Watt Param | Parameterized Frequency-Watt
|  | 128 | Dynamic Reactive Current | Dynamic Reactive Current
|  | 129 | LVRTD | LVRT Must Disconnect
|  | 130 | HVRTD | HVRT Must Disconnect
|  | 131 | Watt-PF | Watt-Power Factor
|  | 132 | Volt-Watt | Volt-Watt
|  | 133 | Basic Scheduling | Basic Scheduling
|  | 134 | Freq-Watt Crv | Curve-Based Frequency-Watt
|  | 135 | LFRT | Low Frequency Ride-through
|  | 136 | HFRT | High Frequency Ride-through
|  | 137 | LVRTC | LVRT must remain connected
|  | 138 | HVRTC | HVRT must remain connected
|  | 139 | LVRTX | LVRT extended curve
|  | 140 | HVRTX | HVRT extended curve
|  | 141 | LFRTC | LFRT must remain connected
|  | 142 | HFRTC | HFRT must remain connected
|  | 143 | LFRTX | LFRT extended curve
|  | 144 | HFRTX | HFRT extended curve
|  | 145 | Extended Settings | Inverter controls extended settings
|  | 160 | Multiple MPPT Inverter Extension Model
|  | 201 | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
|  | 202 | split single phase (ABN) meter
|  | 203 | wye-connect three phase (abcn) meter
|  | 204 | delta-connect three phase (abc) meter
|  | 211 | single phase (AN or AB) meter
|  | 212 | split single phase (ABN) meter
|  | 213 | wye-connect three phase (abcn) meter
|  | 214 | delta-connect three phase (abc) meter
|  | 220 | Secure AC Meter Selected Readings | Include this model for secure metering
|  | 302 | Irradiance Model | Include to support various irradiance measurements
|  | 303 | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
|  | 304 | Inclinometer Model | Include to support orientation measurements
|  | 305 | GPS | Include to support location measurements
|  | 306 | Reference Point Model | Include to support a standard reference point
|  | 307 | Base Met | Base Meteorological Model
|  | 308 | Mini Met Model | Include to support a few basic measurements
|  | 401 | String Combiner (Current) | A basic string combiner
|  | 402 | String Combiner (Advanced) | An advanced string combiner
|  | 403 | String Combiner (Current) | A basic string combiner model
|  | 404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements
|  | 501 | Solar Module | A solar module model supporting DC-DC converter
|  | 502 | Solar Module | A solar module model supporting DC-DC converter
|  | 601 | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers
9C86 | 40070 | 701 | DER AC Measurement | DER AC measurement model.
9D21 | 40225 | 702 | DER Capacity | DER capacity model.
9D55 | 40277 | 703 | Enter Service | Enter service model.
9D68 | 40296 | 704 | DER AC Controls | DER AC controls model.
9DAB | 40363 | 705 | DER Volt-Var | DER Volt-Var model.
9EB4 | 40628 | 706 | DER Volt-Watt | DER Volt-Watt model.
|  | 707 | DER Trip LV | DER low voltage trip model.
|  | 708 | DER Trip HV | DER high voltage trip model.
|  | 709 | DER Trip LF | DER low frequency trip model.
|  | 710 | DER Trip HF | DER high frequency trip model.
|  | 711 | DER Frequency Droop | DER Frequency Droop model.
|  | 712 | DER Watt-Var | DER Watt-Var model.
9FA4 | 40868 | 713 | DER Storage Capacity | DER storage capacity.
|  | 714 | DER DC Measurement | DER DC measurement.
9FAD | 40877 | 715 | DERCtl | DER Control
|  | 801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
9FB6 | 40886 | 802 | Battery Base Model
9FF6 | 40950 | 803 | Lithium-Ion Battery Bank Model
|  | 804 | Lithium-Ion String Model
|  | 805 | Lithium-Ion Module Model
|  | 806 | Flow Battery Model
|  | 807 | Flow Battery String Model
|  | 808 | Flow Battery Module Model
|  | 809 | Flow Battery Stack Model
|  | 63001 | SunSpec Test Model 1
|  | 63002 | SunSpec Test Model 2
|  | 64001 | Veris Status and Configuration
|  | 64020 | Mersen GreenString
A312 | 41746 | 64901 | Socomec PMS | Vendor model providing PMS states, warnings and alarms details
|  | 64902 | Eltek Inverter Extension
|  | 64903 | OutBack AXS device
|  | 64904 | Basic Charge Controller
|  | 64905 | OutBack FM Charge Controller
A344 | 41796 | 64902 | Socomec PMS islanding | Vendor model providing PMS commands for off grid features

## 1
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | common |  |  | group | [6 empty] | Common | All SunSpec compliant devices must include this as the first model
0 |  | ID | 1 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  |  |  | 9C42 | 40002
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  |  |  | 9C43 | 40003
2 |  | Mn |  |  | string | 16 |  |  |  | M | S | Manufacturer | Well known value registered with SunSpec for compliance |  |  |  | 9C44 | 40004
18 |  | Md |  |  | string | 16 |  |  |  | M | S | Model | Manufacturer specific value (32 chars) |  |  |  | 9C54 | 40020
34 |  | Opt |  |  | string | 8 |  |  |  |  | S | Options | Manufacturer specific value (16 chars) |  |  |  | 9C64 | 40036
42 |  | Vr |  |  | string | 8 |  |  |  |  | S | Version | Manufacturer specific value (16 chars) |  |  |  | 9C6C | 40044
50 |  | SN |  |  | string | 16 |  |  |  | M | S | Serial Number | Manufacturer specific value (32 chars) |  |  |  | 9C74 | 40052
66 |  | DA |  |  | uint16 |  |  |  | RW |  |  | Device Address | Modbus device address |  |  |  | 9C84 | 40068
67 |  | Pad |  |  | pad | [5 empty] | S |  | Force even alignment |  |  |  | 9C85 | 40069

## 2 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | aggregator |  |  | group | [6 empty] | Basic Aggregator | Aggregates a collection of models for a given model id
0 |  | ID | 2 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | AID |  |  | uint16 |  |  |  |  | M |  | AID | Aggregated model id
3 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of aggregated models
4 |  | UN |  |  | uint16 |  |  |  |  | M |  | UN | Update Number. Incrementing number each time the mapping is changed. If the number is not changed from the last reading the direct access to a specific offset will result in reading the same logical model as before. Otherwise the entire model must be read to refresh the changes
5 |  | St |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated status code
|  | OFF | 1
|  | ON | 2
|  | FULL | 3
|  | FAULT | 4
6 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Status | Vendor specific status code
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event Code | Bitmask event code
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event Code | Vendor specific event code
11 |  | Ctl |  |  | enum16 | [6 empty] | Control | Control register for all aggregated devices
|  | NONE | 0
|  | AUTOMATIC | 1
|  | FORCE_OFF | 2
|  | TEST | 3
|  | THROTTLE | 4
12 |  | CtlVnd |  |  | enum32 | [6 empty] | Vendor Control | Vendor control register for all aggregated devices
14 |  | CtlVl |  |  | enum32 | [6 empty] | Control Value | Numerical value used as a parameter to the control

## 3 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_3 |  |  | group | [6 empty] | Secure Dataset Read Request | Request a digital signature over a specified set of data registers
0 |  | ID | 3 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of registers being requested
3 |  | Off1 |  |  | uint16 |  |  |  | RW | M |  | Offset1 | Offset of value to read
4 |  | Off2 |  |  | uint16 |  |  |  | RW | M
5 |  | Off3 |  |  | uint16 |  |  |  | RW | M
6 |  | Off4 |  |  | uint16 |  |  |  | RW | M
7 |  | Off5 |  |  | uint16 |  |  |  | RW | M
8 |  | Off6 |  |  | uint16 |  |  |  | RW | M
9 |  | Off7 |  |  | uint16 |  |  |  | RW | M
10 |  | Off8 |  |  | uint16 |  |  |  | RW | M
11 |  | Off9 |  |  | uint16 |  |  |  | RW | M
12 |  | Off10 |  |  | uint16 |  |  |  | RW | M
13 |  | Off11 |  |  | uint16 |  |  |  | RW | M
14 |  | Off12 |  |  | uint16 |  |  |  | RW | M
15 |  | Off13 |  |  | uint16 |  |  |  | RW | M
16 |  | Off14 |  |  | uint16 |  |  |  | RW | M
17 |  | Off15 |  |  | uint16 |  |  |  | RW | M
18 |  | Off16 |  |  | uint16 |  |  |  | RW | M
19 |  | Off17 |  |  | uint16 |  |  |  | RW | M
20 |  | Off18 |  |  | uint16 |  |  |  | RW | M
21 |  | Off19 |  |  | uint16 |  |  |  | RW | M
22 |  | Off20 |  |  | uint16 |  |  |  | RW | M
23 |  | Off21 |  |  | uint16 |  |  |  | RW | M
24 |  | Off22 |  |  | uint16 |  |  |  | RW | M
25 |  | Off23 |  |  | uint16 |  |  |  | RW | M
26 |  | Off24 |  |  | uint16 |  |  |  | RW | M
27 |  | Off25 |  |  | uint16 |  |  |  | RW | M
28 |  | Off26 |  |  | uint16 |  |  |  | RW | M
29 |  | Off27 |  |  | uint16 |  |  |  | RW | M
30 |  | Off28 |  |  | uint16 |  |  |  | RW | M
31 |  | Off29 |  |  | uint16 |  |  |  | RW | M
32 |  | Off30 |  |  | uint16 |  |  |  | RW | M
33 |  | Off31 |  |  | uint16 |  |  |  | RW | M
34 |  | Off32 |  |  | uint16 |  |  |  | RW | M
35 |  | Off33 |  |  | uint16 |  |  |  | RW | M
36 |  | Off34 |  |  | uint16 |  |  |  | RW | M
37 |  | Off35 |  |  | uint16 |  |  |  | RW | M
38 |  | Off36 |  |  | uint16 |  |  |  | RW | M
39 |  | Off37 |  |  | uint16 |  |  |  | RW | M
40 |  | Off38 |  |  | uint16 |  |  |  | RW | M
41 |  | Off39 |  |  | uint16 |  |  |  | RW | M
42 |  | Off40 |  |  | uint16 |  |  |  | RW | M
43 |  | Off41 |  |  | uint16 |  |  |  | RW | M
44 |  | Off42 |  |  | uint16 |  |  |  | RW | M
45 |  | Off43 |  |  | uint16 |  |  |  | RW | M
46 |  | Off44 |  |  | uint16 |  |  |  | RW | M
47 |  | Off45 |  |  | uint16 |  |  |  | RW | M
48 |  | Off46 |  |  | uint16 |  |  |  | RW | M
49 |  | Off47 |  |  | uint16 |  |  |  | RW | M
50 |  | Off48 |  |  | uint16 |  |  |  | RW | M
51 |  | Off49 |  |  | uint16 |  |  |  | RW | M
52 |  | Off50 |  |  | uint16 |  |  |  | RW | M
53 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
55 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
56 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request
57 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Digital Signature ID
58 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
59 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature.
|  | model_3.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M |  | DS | Digital Signature

## 4 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_4 |  |  | group | [6 empty] | Secure Dataset Read Response | Compute a digital signature over a specified set of data registers
0 |  | ID | 4 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | RqSeq |  |  | uint16 |  |  |  |  | M |  | Request Sequence | Sequence number from the request
3 |  | Sts |  |  | enum16 |  |  |  |  | M |  | Status | Status of last read operation
|  | SUCCESS | 0
|  | DS | 1
|  | ACL | 2
|  | OFF | 3
4 |  | X |  |  | uint16 |  |  |  |  | M |  | X | Number of values from the request
5 |  | Val1 |  |  | uint16 |  |  |  |  | M |  | Value1 | Copy of value from register Off1.
6 |  | Val2 |  |  | uint16 |  |  |  |  | M
7 |  | Val3 |  |  | uint16 |  |  |  |  | M
8 |  | Val4 |  |  | uint16 |  |  |  |  | M
9 |  | Val5 |  |  | uint16 |  |  |  |  | M
10 |  | Val6 |  |  | uint16 |  |  |  |  | M
11 |  | Val7 |  |  | uint16 |  |  |  |  | M
12 |  | Val8 |  |  | uint16 |  |  |  |  | M
13 |  | Val9 |  |  | uint16 |  |  |  |  | M
14 |  | Val10 |  |  | uint16 |  |  |  |  | M
15 |  | Val11 |  |  | uint16 |  |  |  |  | M
16 |  | Val12 |  |  | uint16 |  |  |  |  | M
17 |  | Val13 |  |  | uint16 |  |  |  |  | M
18 |  | Val14 |  |  | uint16 |  |  |  |  | M
19 |  | Val15 |  |  | uint16 |  |  |  |  | M
20 |  | Val16 |  |  | uint16 |  |  |  |  | M
21 |  | Val17 |  |  | uint16 |  |  |  |  | M
22 |  | Val18 |  |  | uint16 |  |  |  |  | M
23 |  | Val19 |  |  | uint16 |  |  |  |  | M
24 |  | Val20 |  |  | uint16 |  |  |  |  | M
25 |  | Val21 |  |  | uint16 |  |  |  |  | M
26 |  | Val22 |  |  | uint16 |  |  |  |  | M
27 |  | Val23 |  |  | uint16 |  |  |  |  | M
28 |  | Val24 |  |  | uint16 |  |  |  |  | M
29 |  | Val25 |  |  | uint16 |  |  |  |  | M
30 |  | Val26 |  |  | uint16 |  |  |  |  | M
31 |  | Val27 |  |  | uint16 |  |  |  |  | M
32 |  | Val28 |  |  | uint16 |  |  |  |  | M
33 |  | Val29 |  |  | uint16 |  |  |  |  | M
34 |  | Val30 |  |  | uint16 |  |  |  |  | M
35 |  | Val31 |  |  | uint16 |  |  |  |  | M
36 |  | Val32 |  |  | uint16 |  |  |  |  | M
37 |  | Val33 |  |  | uint16 |  |  |  |  | M
38 |  | Val34 |  |  | uint16 |  |  |  |  | M
39 |  | Val35 |  |  | uint16 |  |  |  |  | M
40 |  | Val36 |  |  | uint16 |  |  |  |  | M
41 |  | Val37 |  |  | uint16 |  |  |  |  | M
42 |  | Val38 |  |  | uint16 |  |  |  |  | M
43 |  | Val39 |  |  | uint16 |  |  |  |  | M
44 |  | Val40 |  |  | uint16 |  |  |  |  | M
45 |  | Val41 |  |  | uint16 |  |  |  |  | M
46 |  | Val42 |  |  | uint16 |  |  |  |  | M
47 |  | Val43 |  |  | uint16 |  |  |  |  | M
48 |  | Val44 |  |  | uint16 |  |  |  |  | M
49 |  | Val45 |  |  | uint16 |  |  |  |  | M
50 |  | Val46 |  |  | uint16 |  |  |  |  | M
51 |  | Val47 |  |  | uint16 |  |  |  |  | M
52 |  | Val48 |  |  | uint16 |  |  |  |  | M
53 |  | Val49 |  |  | uint16 |  |  |  |  | M
54 |  | Val50 |  |  | uint16 |  |  |  |  | M
55 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
57 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
58 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of response
59 |  | Alm |  |  | enum16 |  |  |  |  | M |  | Alarm | Bitmask alarm code
|  | NONE | 0
|  | ALM | 1
60 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
61 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature.
|  | model_4.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M |  | DS | Digital Signature

## 5 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_5 |  |  | group | [6 empty] | Secure Write Request | Include a digital signature along with the control data
0 |  | ID | 5 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of (offset, value) pairs being written
3 |  | Off1 |  |  | uint16 |  |  |  | RW | M |  | Offset1 | Offset of control register to write value to
4 |  | Val1 |  |  | uint16 |  |  |  | RW | M |  | Value1 | Value to write to control register at offset
5 |  | Off2 |  |  | uint16 |  |  |  | RW | M
6 |  | Val2 |  |  | uint16 |  |  |  | RW | M
7 |  | Off3 |  |  | uint16 |  |  |  | RW | M
8 |  | Val3 |  |  | uint16 |  |  |  | RW | M
9 |  | Off4 |  |  | uint16 |  |  |  | RW | M
10 |  | Val4 |  |  | uint16 |  |  |  | RW | M
11 |  | Off5 |  |  | uint16 |  |  |  | RW | M
12 |  | Val5 |  |  | uint16 |  |  |  | RW | M
13 |  | Off6 |  |  | uint16 |  |  |  | RW | M
14 |  | Val6 |  |  | uint16 |  |  |  | RW | M
15 |  | Off7 |  |  | uint16 |  |  |  | RW | M
16 |  | Val7 |  |  | uint16 |  |  |  | RW | M
17 |  | Off8 |  |  | uint16 |  |  |  | RW | M
18 |  | Val8 |  |  | uint16 |  |  |  | RW | M
19 |  | Off9 |  |  | uint16 |  |  |  | RW | M
20 |  | Val9 |  |  | uint16 |  |  |  | RW | M
21 |  | Off10 |  |  | uint16 |  |  |  | RW | M
22 |  | Val10 |  |  | uint16 |  |  |  | RW | M
23 |  | Off11 |  |  | uint16 |  |  |  | RW | M
24 |  | Val11 |  |  | uint16 |  |  |  | RW | M
25 |  | Off12 |  |  | uint16 |  |  |  | RW | M
26 |  | Val12 |  |  | uint16 |  |  |  | RW | M
27 |  | Off13 |  |  | uint16 |  |  |  | RW | M
28 |  | Val13 |  |  | uint16 |  |  |  | RW | M
29 |  | Off14 |  |  | uint16 |  |  |  | RW | M
30 |  | Val14 |  |  | uint16 |  |  |  | RW | M
31 |  | Off15 |  |  | uint16 |  |  |  | RW | M
32 |  | Val15 |  |  | uint16 |  |  |  | RW | M
33 |  | Off16 |  |  | uint16 |  |  |  | RW | M
34 |  | Val16 |  |  | uint16 |  |  |  | RW | M
35 |  | Off17 |  |  | uint16 |  |  |  | RW | M
36 |  | Val17 |  |  | uint16 |  |  |  | RW | M
37 |  | Off18 |  |  | uint16 |  |  |  | RW | M
38 |  | Val18 |  |  | uint16 |  |  |  | RW | M
39 |  | Off19 |  |  | uint16 |  |  |  | RW | M
40 |  | Val19 |  |  | uint16 |  |  |  | RW | M
41 |  | Off20 |  |  | uint16 |  |  |  | RW | M
42 |  | Val20 |  |  | uint16 |  |  |  | RW | M
43 |  | Off21 |  |  | uint16 |  |  |  | RW | M
44 |  | Val21 |  |  | uint16 |  |  |  | RW | M
45 |  | Off22 |  |  | uint16 |  |  |  | RW | M
46 |  | Val22 |  |  | uint16 |  |  |  | RW | M
47 |  | Off23 |  |  | uint16 |  |  |  | RW | M
48 |  | Val23 |  |  | uint16 |  |  |  | RW | M
49 |  | Off24 |  |  | uint16 |  |  |  | RW | M
50 |  | Val24 |  |  | uint16 |  |  |  | RW | M
51 |  | Off25 |  |  | uint16 |  |  |  | RW | M
52 |  | Val25 |  |  | uint16 |  |  |  | RW | M
53 |  | Off26 |  |  | uint16 |  |  |  | RW | M
54 |  | Val26 |  |  | uint16 |  |  |  | RW | M
55 |  | Off27 |  |  | uint16 |  |  |  | RW | M
56 |  | Val27 |  |  | uint16 |  |  |  | RW | M
57 |  | Off28 |  |  | uint16 |  |  |  | RW | M
58 |  | Val28 |  |  | uint16 |  |  |  | RW | M
59 |  | Off29 |  |  | uint16 |  |  |  | RW | M
60 |  | Val29 |  |  | uint16 |  |  |  | RW | M
61 |  | Off30 |  |  | uint16 |  |  |  | RW | M
62 |  | Val30 |  |  | uint16 |  |  |  | RW | M
63 |  | Off31 |  |  | uint16 |  |  |  | RW | M
64 |  | Val31 |  |  | uint16 |  |  |  | RW | M
65 |  | Off32 |  |  | uint16 |  |  |  | RW | M
66 |  | Val32 |  |  | uint16 |  |  |  | RW | M
67 |  | Off33 |  |  | uint16 |  |  |  | RW | M
68 |  | Val33 |  |  | uint16 |  |  |  | RW | M
69 |  | Off34 |  |  | uint16 |  |  |  | RW | M
70 |  | Val34 |  |  | uint16 |  |  |  | RW | M
71 |  | Off35 |  |  | uint16 |  |  |  | RW | M
72 |  | Val35 |  |  | uint16 |  |  |  | RW | M
73 |  | Off36 |  |  | uint16 |  |  |  | RW | M
74 |  | Val36 |  |  | uint16 |  |  |  | RW | M
75 |  | Off37 |  |  | uint16 |  |  |  | RW | M
76 |  | Val37 |  |  | uint16 |  |  |  | RW | M
77 |  | Off38 |  |  | uint16 |  |  |  | RW | M
78 |  | Val38 |  |  | uint16 |  |  |  | RW | M
79 |  | Off39 |  |  | uint16 |  |  |  | RW | M
80 |  | Val39 |  |  | uint16 |  |  |  | RW | M
81 |  | Off40 |  |  | uint16 |  |  |  | RW | M
82 |  | Val40 |  |  | uint16 |  |  |  | RW | M
83 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
85 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
86 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request
87 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5
88 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
89 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature.
|  | model_5.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 6 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_6 |  |  | group | [6 empty] | Secure Write Sequential Request | Include a digital signature along with the control data
0 |  | ID | 6 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | X |  |  | uint16 |  |  |  | RW | M |  | X | Number of (offset, value) pairs being written
3 |  | Off |  |  | uint16 |  |  |  | RW | M |  | Offset | Starting offset for write operation
4 |  | Val1 |  |  | uint16 |  |  |  | RW | M |  | Value1 | Value to write to control register at offset
5 |  | Val2 |  |  | uint16 |  |  |  | RW | M
6 |  | Val3 |  |  | uint16 |  |  |  | RW | M
7 |  | Val4 |  |  | uint16 |  |  |  | RW | M
8 |  | Val5 |  |  | uint16 |  |  |  | RW | M
9 |  | Val6 |  |  | uint16 |  |  |  | RW | M
10 |  | Val7 |  |  | uint16 |  |  |  | RW | M
11 |  | Val8 |  |  | uint16 |  |  |  | RW | M
12 |  | Val9 |  |  | uint16 |  |  |  | RW | M
13 |  | Val10 |  |  | uint16 |  |  |  | RW | M
14 |  | Val11 |  |  | uint16 |  |  |  | RW | M
15 |  | Val12 |  |  | uint16 |  |  |  | RW | M
16 |  | Val13 |  |  | uint16 |  |  |  | RW | M
17 |  | Val14 |  |  | uint16 |  |  |  | RW | M
18 |  | Val15 |  |  | uint16 |  |  |  | RW | M
19 |  | Val16 |  |  | uint16 |  |  |  | RW | M
20 |  | Val17 |  |  | uint16 |  |  |  | RW | M
21 |  | Val18 |  |  | uint16 |  |  |  | RW | M
22 |  | Val19 |  |  | uint16 |  |  |  | RW | M
23 |  | Val20 |  |  | uint16 |  |  |  | RW | M
24 |  | Val21 |  |  | uint16 |  |  |  | RW | M
25 |  | Val22 |  |  | uint16 |  |  |  | RW | M
26 |  | Val23 |  |  | uint16 |  |  |  | RW | M
27 |  | Val24 |  |  | uint16 |  |  |  | RW | M
28 |  | Val25 |  |  | uint16 |  |  |  | RW | M
29 |  | Val26 |  |  | uint16 |  |  |  | RW | M
30 |  | Val27 |  |  | uint16 |  |  |  | RW | M
31 |  | Val28 |  |  | uint16 |  |  |  | RW | M
32 |  | Val29 |  |  | uint16 |  |  |  | RW | M
33 |  | Val30 |  |  | uint16 |  |  |  | RW | M
34 |  | Val31 |  |  | uint16 |  |  |  | RW | M
35 |  | Val32 |  |  | uint16 |  |  |  | RW | M
36 |  | Val33 |  |  | uint16 |  |  |  | RW | M
37 |  | Val34 |  |  | uint16 |  |  |  | RW | M
38 |  | Val35 |  |  | uint16 |  |  |  | RW | M
39 |  | Val36 |  |  | uint16 |  |  |  | RW | M
40 |  | Val37 |  |  | uint16 |  |  |  | RW | M
41 |  | Val38 |  |  | uint16 |  |  |  | RW | M
42 |  | Val39 |  |  | uint16 |  |  |  | RW | M
43 |  | Val40 |  |  | uint16 |  |  |  | RW | M
44 |  | Val41 |  |  | uint16 |  |  |  | RW | M
45 |  | Val42 |  |  | uint16 |  |  |  | RW | M
46 |  | Val43 |  |  | uint16 |  |  |  | RW | M
47 |  | Val44 |  |  | uint16 |  |  |  | RW | M
48 |  | Val45 |  |  | uint16 |  |  |  | RW | M
49 |  | Val46 |  |  | uint16 |  |  |  | RW | M
50 |  | Val47 |  |  | uint16 |  |  |  | RW | M
51 |  | Val48 |  |  | uint16 |  |  |  | RW | M
52 |  | Val49 |  |  | uint16 |  |  |  | RW | M
53 |  | Val50 |  |  | uint16 |  |  |  | RW | M
54 |  | Val51 |  |  | uint16 |  |  |  | RW | M
55 |  | Val52 |  |  | uint16 |  |  |  | RW | M
56 |  | Val53 |  |  | uint16 |  |  |  | RW | M
57 |  | Val54 |  |  | uint16 |  |  |  | RW | M
58 |  | Val55 |  |  | uint16 |  |  |  | RW | M
59 |  | Val56 |  |  | uint16 |  |  |  | RW | M
60 |  | Val57 |  |  | uint16 |  |  |  | RW | M
61 |  | Val58 |  |  | uint16 |  |  |  | RW | M
62 |  | Val59 |  |  | uint16 |  |  |  | RW | M
63 |  | Val60 |  |  | uint16 |  |  |  | RW | M
64 |  | Val61 |  |  | uint16 |  |  |  | RW | M
65 |  | Val62 |  |  | uint16 |  |  |  | RW | M
66 |  | Val63 |  |  | uint16 |  |  |  | RW | M
67 |  | Val64 |  |  | uint16 |  |  |  | RW | M
68 |  | Val65 |  |  | uint16 |  |  |  | RW | M
69 |  | Val66 |  |  | uint16 |  |  |  | RW | M
70 |  | Val67 |  |  | uint16 |  |  |  | RW | M
71 |  | Val68 |  |  | uint16 |  |  |  | RW | M
72 |  | Val69 |  |  | uint16 |  |  |  | RW | M
73 |  | Val70 |  |  | uint16 |  |  |  | RW | M
74 |  | Val71 |  |  | uint16 |  |  |  | RW | M
75 |  | Val72 |  |  | uint16 |  |  |  | RW | M
76 |  | Val73 |  |  | uint16 |  |  |  | RW | M
77 |  | Val74 |  |  | uint16 |  |  |  | RW | M
78 |  | Val75 |  |  | uint16 |  |  |  | RW | M
79 |  | Val76 |  |  | uint16 |  |  |  | RW | M
80 |  | Val77 |  |  | uint16 |  |  |  | RW | M
81 |  | Val78 |  |  | uint16 |  |  |  | RW | M
82 |  | Val79 |  |  | uint16 |  |  |  | RW | M
83 |  | Val80 |  |  | uint16 |  |  |  | RW | M
84 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
86 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
87 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request
88 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5
89 |  | Rsrvd |  |  | pad |  |  |  | RW | M
90 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
91 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature.
|  | model_6.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 7 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_7 |  |  | group | [6 empty] | Secure Write Response Model (DRAFT 1) | Include a digital signature over the response
0 |  | ID | 7 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | RqSeq |  |  | uint16 |  |  |  |  | M |  | Request Sequence | Sequence number from the request
3 |  | Sts |  |  | enum16 |  |  |  |  | M |  | Status | Status of last write operation
|  | SUCCESS | 0
|  | DS | 1
|  | ACL | 2
|  | OFF | 3
|  | VAL | 4
4 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
6 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
7 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of response
8 |  | Alm |  |  | enum16 |  |  |  |  | M |  | Alarm | Bitmask alarm code
|  | NONE | 0
|  | ALM | 1
9 |  | Rsrvd |  |  | pad |  |  |  |  | M
10 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
11 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers comprising the digital signature.
|  | model_7.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  | RW | M |  | DS | Digital Signature

## 8 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_8 |  |  | group | [6 empty] | Get Device Security Certificate | Security model for PKI
0 |  | ID | 8 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Fmt |  |  | enum16 |  |  |  |  | M |  | Format | X.509 format of the certificate. DER or PEM.
|  | NONE | 0
|  | X509_PEM | 1
|  | X509_DER | 2
3 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers to follow for the certificate
|  | model_8.repeating |  | 0 | group
| 0 | Cert |  |  | uint16 |  |  |  |  | M |  | Cert | X.509 Certificate of the device

## 9 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_9 |  |  | group | [6 empty] | Set Operator Security Certificate | Security model for PKI
0 |  | ID | 9 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | CertUID |  |  | uint16 |  |  |  | RW | M |  | Cert_UID | User ID for this certificate
3 |  | CertRole |  |  | uint16 |  |  |  | RW | M |  | Cert_Role | Role for this certificate
4 |  | Fmt |  |  | enum16 |  |  |  | RW | M |  | Format | Format of this certificate
|  | NONE | 0
|  | X509_PEM | 1
|  | X509_DER | 2
5 |  | Typ |  |  | enum16 |  |  |  | RW | M |  | Type | Type of this certificate
|  | DEV_KEY_PAIR | 0
|  | DEV_SHARED_KEY | 1
|  | OPERATOR_PUB | 2
|  | OPERATOR_SHARED | 3
|  | CA_PUB | 4
6 |  | TotLn |  |  | uint16 |  |  |  | RW | M |  | Total Length | Total Length of the Certificate
7 |  | FrgLn |  |  | uint16 |  |  |  | RW | M |  | Fragment length | Length of this fragment
8 |  | Frg1 |  |  | uint16 |  |  |  | RW | M |  | Frag1 | First word of this fragment
9 |  | Frg2 |  |  | uint16 |  |  |  | RW | M
10 |  | Frg3 |  |  | uint16 |  |  |  | RW | M
11 |  | Frg4 |  |  | uint16 |  |  |  | RW | M
12 |  | Frg5 |  |  | uint16 |  |  |  | RW | M
13 |  | Frg6 |  |  | uint16 |  |  |  | RW | M
14 |  | Frg7 |  |  | uint16 |  |  |  | RW | M
15 |  | Frg8 |  |  | uint16 |  |  |  | RW | M
16 |  | Frg9 |  |  | uint16 |  |  |  | RW | M
17 |  | Frg10 |  |  | uint16 |  |  |  | RW | M
18 |  | Frg11 |  |  | uint16 |  |  |  | RW | M
19 |  | Frg12 |  |  | uint16 |  |  |  | RW | M
20 |  | Frg13 |  |  | uint16 |  |  |  | RW | M
21 |  | Frg14 |  |  | uint16 |  |  |  | RW | M
22 |  | Frg15 |  |  | uint16 |  |  |  | RW | M
23 |  | Frg16 |  |  | uint16 |  |  |  | RW | M
24 |  | Frg17 |  |  | uint16 |  |  |  | RW | M
25 |  | Frg18 |  |  | uint16 |  |  |  | RW | M
26 |  | Frg19 |  |  | uint16 |  |  |  | RW | M
27 |  | Frg20 |  |  | uint16 |  |  |  | RW | M
28 |  | Frg21 |  |  | uint16 |  |  |  | RW | M
29 |  | Frg22 |  |  | uint16 |  |  |  | RW | M
30 |  | Frg23 |  |  | uint16 |  |  |  | RW | M
31 |  | Frg24 |  |  | uint16 |  |  |  | RW | M
32 |  | Frg25 |  |  | uint16 |  |  |  | RW | M
33 |  | Frg26 |  |  | uint16 |  |  |  | RW | M
34 |  | Frg27 |  |  | uint16 |  |  |  | RW | M
35 |  | Frg28 |  |  | uint16 |  |  |  | RW | M
36 |  | Frg29 |  |  | uint16 |  |  |  | RW | M
37 |  | Frg30 |  |  | uint16 |  |  |  | RW | M
38 |  | Frg31 |  |  | uint16 |  |  |  | RW | M
39 |  | Frg32 |  |  | uint16 |  |  |  | RW | M
40 |  | Frg33 |  |  | uint16 |  |  |  | RW | M
41 |  | Frg34 |  |  | uint16 |  |  |  | RW | M
42 |  | Frg35 |  |  | uint16 |  |  |  | RW | M
43 |  | Frg36 |  |  | uint16 |  |  |  | RW | M
44 |  | Frg37 |  |  | uint16 |  |  |  | RW | M
45 |  | Frg38 |  |  | uint16 |  |  |  | RW | M
46 |  | Frg39 |  |  | uint16 |  |  |  | RW | M
47 |  | Frg40 |  |  | uint16 |  |  |  | RW | M
48 |  | Frg41 |  |  | uint16 |  |  |  | RW | M
49 |  | Frg42 |  |  | uint16 |  |  |  | RW | M
50 |  | Frg43 |  |  | uint16 |  |  |  | RW | M
51 |  | Frg44 |  |  | uint16 |  |  |  | RW | M
52 |  | Frg45 |  |  | uint16 |  |  |  | RW | M
53 |  | Frg46 |  |  | uint16 |  |  |  | RW | M
54 |  | Frg47 |  |  | uint16 |  |  |  | RW | M
55 |  | Frg48 |  |  | uint16 |  |  |  | RW | M
56 |  | Frg49 |  |  | uint16 |  |  |  | RW | M
57 |  | Frg50 |  |  | uint16 |  |  |  | RW | M
58 |  | Frg51 |  |  | uint16 |  |  |  | RW | M
59 |  | Frg52 |  |  | uint16 |  |  |  | RW | M
60 |  | Frg53 |  |  | uint16 |  |  |  | RW | M
61 |  | Frg54 |  |  | uint16 |  |  |  | RW | M
62 |  | Frg55 |  |  | uint16 |  |  |  | RW | M
63 |  | Frg56 |  |  | uint16 |  |  |  | RW | M
64 |  | Frg57 |  |  | uint16 |  |  |  | RW | M
65 |  | Frg58 |  |  | uint16 |  |  |  | RW | M
66 |  | Frg59 |  |  | uint16 |  |  |  | RW | M
67 |  | Frg60 |  |  | uint16 |  |  |  | RW | M
68 |  | Frg61 |  |  | uint16 |  |  |  | RW | M
69 |  | Frg62 |  |  | uint16 |  |  |  | RW | M
70 |  | Frg63 |  |  | uint16 |  |  |  | RW | M
71 |  | Frg64 |  |  | uint16 |  |  |  | RW | M
72 |  | Frg65 |  |  | uint16 |  |  |  | RW | M
73 |  | Frg66 |  |  | uint16 |  |  |  | RW | M
74 |  | Frg67 |  |  | uint16 |  |  |  | RW | M
75 |  | Frg68 |  |  | uint16 |  |  |  | RW | M
76 |  | Frg69 |  |  | uint16 |  |  |  | RW | M
77 |  | Frg70 |  |  | uint16 |  |  |  | RW | M
78 |  | Frg71 |  |  | uint16 |  |  |  | RW | M
79 |  | Frg72 |  |  | uint16 |  |  |  | RW | M
80 |  | Frg73 |  |  | uint16 |  |  |  | RW | M
81 |  | Frg74 |  |  | uint16 |  |  |  | RW | M
82 |  | Frg75 |  |  | uint16 |  |  |  | RW | M
83 |  | Frg78 |  |  | uint16 |  |  |  | RW | M
84 |  | Frg79 |  |  | uint16 |  |  |  | RW | M
85 |  | Frg80 |  |  | uint16 |  |  |  | RW | M |  | Frag80 | Last word of this fragment
86 |  | Ts |  |  | uint32 |  |  |  | RW | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
88 |  | Ms |  |  | uint16 |  |  |  | RW | M |  | Milliseconds | Millisecond counter 0-999
89 |  | Seq |  |  | uint16 |  |  |  | RW | M |  | Sequence | Sequence number of request
90 |  | UID |  |  | uint16 |  |  |  | RW | M |  | UID | User ID for the request signature
91 |  | Role |  |  | uint16 |  |  |  | RW | M |  | Role | Signing key used 0-5
92 |  | Alg |  |  | enum16 |  |  |  | RW | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
93 |  | N |  |  | uint16 |  |  |  | RW | M |  | N | Number of registers to follow for the certificate
|  | model_9.repeating |  | 0 | group
| 0 | Cert |  |  | uint16 |  |  |  | RW | M

## 10 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_10 |  |  | group | [6 empty] | Communication Interface Header | To be included first for a complete interface description
0 |  | ID | 10 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | St |  |  | enum16 |  |  |  |  | M |  | Interface Status | Overall interface status
|  | DOWN | 0
|  | UP | 1
|  | FAULT | 2
3 |  | Ctl |  |  | uint16 |  |  |  | RW |  |  | Interface Control | Overall interface control (TBD)
4 |  | Typ |  |  | enum16 | [6 empty] | Physical Access Type | Enumerated value. Type of physical media
|  | UNKNOWN | 0
|  | INTERNAL | 1
|  | TWISTED_PAIR | 2
|  | FIBER | 3
|  | WIRELESS | 4
5 |  | Pad |  |  | pad

## 11 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_11 |  |  | group | [6 empty] | Ethernet Link Layer | Include to support a wired ethernet port
0 |  | ID | 11 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Spd |  |  | uint16 |  |  | Mbps |  | M |  | Ethernet Link Speed | Interface speed in Mb/s
3 |  | CfgSt |  |  | bitfield16 |  |  |  |  | M |  | Interface Status Flags | Bitmask values Interface flags.
|  | LINK | 0
|  | FULL_DUPLEX | 1
|  | AUTO_NEG1 | 2
|  | AUTO_NEG2 | 3
|  | AUTO_NEG3 | 4
|  | RESET_REQUIRED | 5
|  | HW_FAULT | 6
4 |  | St |  |  | enum16 |  |  |  |  | M |  | Link State | Enumerated value. State information for this interface
|  | UNKNOWN | 0
|  | ENABLED | 1
|  | DISABLED | 2
|  | TESTING | 3
5 |  | MAC |  |  | eui48 | [6 empty] | MAC | IEEE MAC address of this interface
9 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name (8 chars)
13 |  | Ctl |  |  | bitfield16 |  |  |  | RW |  |  | Control | Control flags
|  | AUTO | 0
|  | FULL_DUPLEX | 1
14 |  | FrcSpd |  |  | uint16 |  |  | Mbps | RW |  |  | Forced Speed | Forced interface speed in Mb/s when AUTO is disabled

## 12 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_12 |  |  | group | [6 empty] | IPv4 | Include to support an IPv4 protocol stack on this interface
0 |  | ID | 12 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | CfgSt |  |  | enum16 |  |  |  |  | M |  | Config Status | Enumerated value. Configuration status
|  | NOT_CONFIGURED | 0
|  | VALID_SETTING | 1
|  | VALID_HW | 2
7 |  | ChgSt |  |  | bitfield16 |  |  |  |  | M |  | Change Status | Bitmask value. A configuration change is pending
|  | PENDING | 0
8 |  | Cap |  |  | bitfield16 |  |  |  |  | M |  | Config Capability | Bitmask value. Identify capable sources of configuration
|  | DHCP | 0
|  | BOOTP | 1
|  | ZEROCONF | 2
|  | DNS | 3
|  | CFG_SETTABLE | 4
|  | HW_CONFIG | 5
|  | NTP_CLIENT | 6
|  | RESET_REQUIRED | 7
9 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | IPv4 Config | Enumerated value. Configuration method used.
|  | STATIC | 0
|  | DHCP | 1
|  | BOOTP | 2
|  | ZEROCONF | 3
10 |  | Ctl |  |  | enum16 |  |  |  | RW | M |  | Control | Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
11 |  | Addr |  |  | string | 8 |  |  | RW | M |  | IP | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx
19 |  | Msk |  |  | string | 8 |  |  | RW | M |  | Netmask | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx
27 |  | Gw |  |  | string | 8 |  |  | RW |  |  | Gateway | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx
35 |  | DNS1 |  |  | string | 8 |  |  | RW |  |  | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
43 |  | DNS2 |  |  | string | 8 |  |  | RW |  |  | DNS2 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx
51 |  | NTP1 |  |  | string | 12 |  |  | RW |  |  | NTP1 | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
63 |  | NTP2 |  |  | string | 12 |  |  | RW |  |  | NTP2 | IPv4 numeric NTP address as a dotted string xxx.xxx.xxx.xxx
75 |  | DomNam |  |  | string | 12 |  |  | RW |  |  | Domain | Domain name (24 chars max)
87 |  | HostNam |  |  | string | 12 |  |  | RW |  |  | Host Name | Host name (24 chars max)
99 |  | Pad |  |  | pad

## 13 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_13 |  |  | group | [6 empty] | IPv6 | Include to support an IPv6 protocol stack on this interface
0 |  | ID | 13 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | CfgSt |  |  | enum16 |  |  |  |  | M |  | Config Status | Enumerated value. Configuration status
|  | NOT_CONFIGURED | 0
|  | VALID_SETTING | 1
|  | VALID_HW | 2
7 |  | ChgSt |  |  | bitfield16 |  |  |  |  | M |  | Change Status | Bitmask value. A configuration change is pending
|  | PENDING | 0
8 |  | Cap |  |  | bitfield16 |  |  |  |  | M |  | Config Capability | Bitmask value. Identify capable sources of configuration
|  | DHCP | 0
|  | BOOTP | 1
|  | ZEROCONF | 2
|  | DNS | 3
|  | CFG_SETTABLE | 4
|  | HW_CONFIG | 5
|  | NTP_CLIENT | 6
|  | RESET_REQUIRED | 7
9 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | IPv6 Config | Enumerated value. Configuration method used.
|  | STATIC | 0
|  | DHCP | 1
|  | BOOTP | 2
|  | ZEROCONF | 3
10 |  | Ctl |  |  | enum16 |  |  |  | RW | M |  | Control | Bitmask value. Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
11 |  | Addr |  |  | string | 20 |  |  | RW | M |  | IP | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
31 |  | CIDR |  |  | string | 20 |  |  | RW |  |  | CIDR | Classless Inter-Domain Routing Number
51 |  | Gw |  |  | string | 20 |  |  | RW |  |  | Gateway | IPv6 numeric address as a dotted string xxxx.xxxx.xxxx.xxxx
71 |  | DNS1 |  |  | string | 20 |  |  | RW |  |  | DNS1 | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
91 |  | DNS2 |  |  | string | 20 |  |  | RW |  |  | DNS2 | IPv6 numeric DNS address as a dotted string xxxx.xxxx.xxxx.xxxx
111 |  | NTP1 |  |  | string | 20 |  |  | RW |  |  | NTP1 | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
131 |  | NTP2 |  |  | string | 20 |  |  | RW |  |  | NTP2 | IPv6 numeric NTP address as a name or dotted string xxxx.xxxx.xxxx.xxxx
151 |  | DomNam |  |  | string | 12 |  |  | RW |  |  | Domain | Domain name (24 chars max)
163 |  | HostNam |  |  | string | 12 |  |  | RW |  |  | Host Name | Host name (24 chars max)
175 |  | Pad |  |  | pad

## 14 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_14 |  |  | group | [6 empty] | Proxy Server | Include this block to allow for a proxy server
0 |  | ID | 14 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | name | Interface name (8 chars)
6 |  | Cap |  |  | bitfield16 |  |  |  | RW | M |  | Capabilities | Bitmask value. Proxy configuration capabilities
|  | NO_PROXY | 0
|  | IPV4_PROXY | 1
|  | IPV6_PROXY | 2
7 |  | Cfg |  |  | enum16 |  |  |  | RW | M |  | Config | Enumerated value. Set proxy address type
8 |  | Typ |  |  | bitfield16 |  |  |  | RW | M |  | Type | Enumerate value. Proxy server type
9 |  | Addr |  |  | string | 20 |  |  | RW | M |  | Address | IPv4 or IPv6 proxy hostname or dotted address (40 chars)
29 |  | Port |  |  | uint16 |  |  |  | RW | M |  | Port | Proxy port number
30 |  | User |  |  | string | 12 |  |  | RW |  |  | Username | Proxy user name
42 |  | Pw |  |  | string | 12 |  |  | RW |  |  | Password | Proxy password

## 15 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_15 |  |  | group | [6 empty] | Interface Counters Model | Interface counters
0 |  | ID | 15 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Clr |  |  | uint16 |  |  |  | RW |  |  | Clear | Write a "1" to clear all counters
3 |  | InCnt |  |  | acc32 | [6 empty] | Input Count | Number of bytes received
5 |  | InUcCnt |  |  | acc32 | [6 empty] | Input Unicast Count | Number of Unicast packets received
7 |  | InNUcCnt |  |  | acc32 | [6 empty] | Input Non-Unicast Count | Number of non-Unicast packets received
9 |  | InDscCnt |  |  | acc32 | [6 empty] | Input Discarded Count | Number of inbound packets received on the interface but discarded
11 |  | InErrCnt |  |  | acc32 | [6 empty] | Input Error Count | Number of inbound packets that contain errors (excluding discards)
13 |  | InUnkCnt |  |  | acc32 | [6 empty] | Input Unknown Count | Number of inbound packets with unknown protocol
15 |  | OutCnt |  |  | acc32 | [6 empty] | Output Count | Total number of bytes transmitted on this interface
17 |  | OutUcCnt |  |  | acc32 | [6 empty] | Output Unicast Count | Number of Unicast packets transmitted
19 |  | OutNUcCnt |  |  | acc32 | [6 empty] | Output Non-Unicast Count | Number of Non-Unicast packets transmitted
21 |  | OutDscCnt |  |  | acc32 | [6 empty] | Output Discarded Count | Number of Discarded output packets
23 |  | OutErrCnt |  |  | acc32 | [6 empty] | Output Error Count | Number of outbound error packets
25 |  | Pad |  |  | pad

## 16 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_16 |  |  | group | [6 empty] | Simple IP Network | Include this model for a simple IPv4 network stack
0 |  | ID | 16 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name. (8 chars)
6 |  | Cfg |  |  | enum16 |  |  |  |  | M |  | Config | Enumerated value. Force IPv4 configuration method
|  | STATIC | 0
|  | DHCP | 1
7 |  | Ctl |  |  | bitfield16 |  |  |  | RW | M |  | Control | Bitmask value Configure use of services
|  | ENABLE_DNS | 0
|  | ENABLE_NTP | 1
8 |  | Addr |  |  | string | 8 |  |  | RW | M |  | Address | IP address
16 |  | Msk |  |  | string | 8 |  |  | RW | M |  | Netmask | Netmask
24 |  | Gw |  |  | string | 8 |  |  | RW |  |  | Gateway | Gateway IP address
32 |  | DNS1 |  |  | string | 8 |  |  | RW |  |  | DNS1 | 32 bit IP address of DNS server
40 |  | DNS2 |  |  | string | 8 |  |  | RW |  |  | DNS2 | 32 bit IP address of DNS server
48 |  | MAC |  |  | eui48 | [6 empty] | MAC | IEEE MAC address of this interface
52 |  | LnkCtl |  |  | bitfield16 |  |  |  | RW |  |  | Link Control | Bitmask value. Link control flags
|  | AUTONEGOTIATE | 0
|  | FULL_DUPLEX | 1
|  | FORCE_10MB | 2
|  | FORCE_100MB | 3
|  | FORCE_1GB | 4
53 |  | Pad |  |  | pad

## 17 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_17 |  |  | group | [6 empty] | Serial Interface | Include this model for serial interface configuration support
0 |  | ID | 17 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name (8 chars)
6 |  | Rte |  |  | uint32 |  |  | bps | RW | M |  | Rate | Interface baud rate in bits per second
8 |  | Bits |  |  | uint16 |  |  |  | RW | M |  | Bits | Number of data bits per character
9 |  | Pty |  |  | enum16 |  |  |  | RW | M |  | Parity | Bitmask value. Parity setting
|  | NONE | 0
|  | ODD | 1
|  | EVEN | 2
10 |  | Dup |  |  | enum16 |  |  |  | RW |  |  | Duplex | Enumerated value. Duplex mode
|  | FULL | 0
|  | HALF | 1
11 |  | Flw |  |  | enum16 |  |  |  | RW |  |  | Flow Control | Flow Control Method
|  | NONE | 0
|  | HW | 1
|  | XONXOFF | 2
12 |  | Typ |  |  | enum16 | [6 empty] | Interface Type | Enumerated value. Interface type
|  | UNKNOWN | 0
|  | RS232 | 1
|  | RS485 | 2
13 |  | Pcol |  |  | enum16 | [6 empty] | Protocol | Enumerated value. Serial protocol selection
|  | UNKNOWN | 0
|  | MODBUS | 1
|  | VENDOR | 2

## 18 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_18 |  |  | group | [6 empty] | Cellular Link | Include this model to support a cellular interface link
0 |  | ID | 18 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | IMEI |  |  | uint32 |  |  |  | RW |  |  | IMEI | International Mobile Equipment Identifier for the interface
8 |  | APN |  |  | string | 4 |  |  | RW |  |  | APN | Access Point Name for the interface
12 |  | Num |  |  | string | 6 |  |  | RW |  |  | Number | Phone number for the interface
18 |  | Pin |  |  | string | 6 |  |  | RW |  |  | PIN | Personal Identification Number for the interface

## 19 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_19 |  |  | group | [6 empty] | PPP Link | Include this model to configure a Point-to-Point Protocol link
0 |  | ID | 19 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 4 |  |  | RW |  |  | Name | Interface name
6 |  | Rte |  |  | uint32 |  |  | bps | RW | M |  | Rate | Interface baud rate in bits per second
8 |  | Bits |  |  | uint16 |  |  |  | RW | M |  | Bits | Number of data bits per character
9 |  | Pty |  |  | enum16 |  |  |  | RW | M |  | Parity | Bitmask value. Parity setting
|  | NONE | 0
|  | ODD | 1
|  | EVEN | 2
10 |  | Dup |  |  | enum16 |  |  |  | RW |  |  | Duplex | Enumerated value. Duplex mode
|  | FULL | 0
|  | HALF | 1
11 |  | Flw |  |  | enum16 |  |  |  | RW |  |  | Flow Control | Flow Control Method
|  | NONE | 0
|  | HW | 1
|  | XONXOFF | 2
12 |  | Auth |  |  | enum16 | [6 empty] | Authentication | Enumerated value. Authentication method
|  | NONE | 0
|  | PAP | 1
|  | CHAP | 2
13 |  | UsrNam |  |  | string | 12 | [5 empty] | Username | Username for authentication
25 |  | Pw |  |  | string | 6 | [5 empty] | Password | Password for authentication
31 |  | Pad |  |  | pad

## 101 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Single Phase) | Include this model for single phase inverter monitoring
0 |  | ID | 101 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 102 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
0 |  | ID | 102 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | uint16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 103 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Three Phase) | Include this model for three phase inverter monitoring
0 |  | ID | 103 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | uint16 |  | A_SF | A |  | M |  | Amps | AC Current
3 |  | AphA |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | uint16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M
7 |  | PPVphAB |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
8 |  | PPVphBC |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
9 |  | PPVphCA |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
10 |  | PhVphA |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
11 |  | PhVphB |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
12 |  | PhVphC |  |  | uint16 |  | V_SF | V |  | M |  | Phase Voltage CN | Phase Voltage CN
13 |  | V_SF |  |  | sunssf |  |  |  |  | M
14 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | AC Power
15 |  | W_SF |  |  | sunssf |  |  |  |  | M
16 |  | Hz |  |  | uint16 |  | Hz_SF | Hz |  | M |  | Hz | Line Frequency
17 |  | Hz_SF |  |  | sunssf |  |  |  |  | M
18 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
19 |  | VA_SF |  |  | sunssf
20 |  | VAr |  |  | int16 |  | VAr_SF | var |  |  |  | VAr | AC Reactive Power
21 |  | VAr_SF |  |  | sunssf
22 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | AC Power Factor
23 |  | PF_SF |  |  | sunssf
24 |  | WH |  |  | acc32 |  | WH_SF | Wh |  | M |  | WattHours | AC Energy
26 |  | WH_SF |  |  | sunssf |  |  |  |  | M
27 |  | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Amps | DC Current
28 |  | DCA_SF |  |  | sunssf
29 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage | DC Voltage
30 |  | DCV_SF |  |  | sunssf
31 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | DC Watts | DC Power
32 |  | DCW_SF |  |  | sunssf
33 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  | M |  | Cabinet Temperature | Cabinet Temperature
34 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
35 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer Temperature
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other Temperature
37 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M
38 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
39 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
40 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
42 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
44 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
46 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
48 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
50 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 111 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Single Phase) FLOAT | Include this model for single phase inverter monitoring using float values
0 |  | ID | 111 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  |  |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | ggOFF | 1
|  | ggSLEEPING | 2
|  | ggSTARTING | 3
|  | ggMPPT | 4
|  | ggTHROTTLED | 5
|  | ggSHUTTING_DOWN | 6
|  | ggFAULT | 7
|  | ggSTANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 112 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Split Phase) FLOAT | Include this model for split phase inverter monitoring using float values
0 |  | ID | 112 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 113 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inverter |  |  | group | [6 empty] | Inverter (Three Phase) FLOAT | Include this model for three phase inverter monitoring using float values
0 |  | ID | 113 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
10 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
12 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
16 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
18 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
20 |  | PhVphC |  |  | float32 |  |  | V |  | M |  | Phase Voltage CN | Phase Voltage CN
22 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | AC Power
24 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Line Frequency
26 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
28 |  | VAr |  |  | float32 |  |  | var |  |  |  | VAr | AC Reactive Power
30 |  | PF |  |  | float32 |  |  | Pct |  |  |  | PF | AC Power Factor
32 |  | WH |  |  | float32 |  |  | Wh |  | M |  | WattHours | AC Energy
34 |  | DCA |  |  | float32 |  |  | A |  |  |  | DC Amps | DC Current
36 |  | DCV |  |  | float32 |  |  | V |  |  |  | DC Voltage | DC Voltage
38 |  | DCW |  |  | float32 |  |  | W |  |  |  | DC Watts | DC Power
40 |  | TmpCab |  |  | float32 |  |  | C |  | M |  | Cabinet Temperature | Cabinet Temperature
42 |  | TmpSnk |  |  | float32 |  |  | C |  |  |  | Heat Sink Temperature | Heat Sink Temperature
44 |  | TmpTrns |  |  | float32 |  |  | C |  |  |  | Transformer Temperature | Transformer Temperature
46 |  | TmpOt |  |  | float32 |  |  | C |  |  |  | Other Temperature | Other Temperature
48 |  | St |  |  | enum16 |  |  |  |  | M |  | Operating State | Enumerated value. Operating state
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
49 |  | StVnd |  |  | enum16 | [6 empty] | Vendor Operating State | Vendor specific operating state code
50 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Event1 | Bitmask value. Event fields
|  | GROUND_FAULT | 0
|  | DC_OVER_VOLT | 1
|  | AC_DISCONNECT | 2
|  | DC_DISCONNECT | 3
|  | GRID_DISCONNECT | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | OVER_FREQUENCY | 8
|  | UNDER_FREQUENCY | 9
|  | AC_OVER_VOLT | 10
|  | AC_UNDER_VOLT | 11
|  | BLOWN_STRING_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | HW_TEST_FAILURE | 15
52 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Event Bitfield 2 | Reserved for future use
54 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events
56 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events
58 |  | EvtVnd3 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 3 | Vendor defined events
60 |  | EvtVnd4 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 4 | Vendor defined events

## 120 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | nameplate |  |  | group | [6 empty] | Nameplate | Inverter Controls Nameplate Ratings
0 |  | ID | 120 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DERTyp |  |  | enum16 |  |  |  |  | M |  | DERTyp | Type of DER device. Default value is 4 to indicate PV device.
|  | PV | 4
|  | PV_STOR | 82
3 |  | WRtg |  |  | uint16 |  | WRtg_SF | W |  | M |  | WRtg | Continuous power output capability of the inverter.
4 |  | WRtg_SF |  |  | sunssf |  |  |  |  | M |  | WRtg_SF | Scale factor
5 |  | VARtg |  |  | uint16 |  | VARtg_SF | VA |  | M |  | VARtg | Continuous Volt-Ampere capability of the inverter.
6 |  | VARtg_SF |  |  | sunssf |  |  |  |  | M |  | VARtg_SF | Scale factor
7 |  | VArRtgQ1 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1.
8 |  | VArRtgQ2 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2.
9 |  | VArRtgQ3 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3.
10 |  | VArRtgQ4 |  |  | int16 |  | VArRtg_SF | var |  | M |  | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4.
11 |  | VArRtg_SF |  |  | sunssf |  |  |  |  | M |  | VArRtg_SF | Scale factor
12 |  | ARtg |  |  | uint16 |  | ARtg_SF | A |  | M |  | ARtg | Maximum RMS AC current level capability of the inverter.
13 |  | ARtg_SF |  |  | sunssf |  |  |  |  | M |  | ARtg_SF | Scale factor
14 |  | PFRtgQ1 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1.
15 |  | PFRtgQ2 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2.
16 |  | PFRtgQ3 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3.
17 |  | PFRtgQ4 |  |  | int16 |  | PFRtg_SF | cos() |  | M |  | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4.
18 |  | PFRtg_SF |  |  | sunssf |  |  |  |  | M |  | PFRtg_SF | Scale factor
19 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  |  |  | WHRtg | Nominal energy rating of storage device.
20 |  | WHRtg_SF |  |  | sunssf | [6 empty] | WHRtg_SF | Scale factor
21 |  | AhrRtg |  |  | uint16 |  | AhrRtg_SF | AH |  |  |  | AhrRtg | The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
22 |  | AhrRtg_SF |  |  | sunssf | [6 empty] | AhrRtg_SF | Scale factor for amp-hour rating.
23 |  | MaxChaRte |  |  | uint16 |  | MaxChaRte_SF | W |  |  |  | MaxChaRte | Maximum rate of energy transfer into the storage device.
24 |  | MaxChaRte_SF |  |  | sunssf | [6 empty] | MaxChaRte_SF | Scale factor
25 |  | MaxDisChaRte |  |  | uint16 |  | MaxDisChaRte_SF | W |  |  |  | MaxDisChaRte | Maximum rate of energy transfer out of the storage device.
26 |  | MaxDisChaRte_SF |  |  | sunssf | [6 empty] | MaxDisChaRte_SF | Scale factor
27 |  | Pad |  |  | pad | [6 empty] | Pad | Pad register.

## 121 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | settings |  |  | group | [6 empty] | Basic Settings | Inverter Controls Basic Settings
0 |  | ID | 121 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WMax |  |  | uint16 |  | WMax_SF | W | RW | M |  | WMax | Setting for maximum power output. Default to WRtg.
3 |  | VRef |  |  | uint16 |  | VRef_SF | V | RW | M |  | VRef | Voltage at the PCC.
4 |  | VRefOfs |  |  | int16 |  | VRefOfs_SF | V | RW | M |  | VRefOfs | Offset from PCC to inverter.
5 |  | VMax |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMax | Setpoint for maximum voltage.
6 |  | VMin |  |  | uint16 |  | VMinMax_SF | V | RW |  |  | VMin | Setpoint for minimum voltage.
7 |  | VAMax |  |  | uint16 |  | VAMax_SF | VA | RW |  |  | VAMax | Setpoint for maximum apparent power. Default to VARtg.
8 |  | VArMaxQ1 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ1 | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1.
9 |  | VArMaxQ2 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ2 | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.
10 |  | VArMaxQ3 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ3 | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.
11 |  | VArMaxQ4 |  |  | int16 |  | VArMax_SF | var | RW |  |  | VArMaxQ4 | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.
12 |  | WGra |  |  | uint16 |  | WGra_SF | % WMax/sec | RW |  |  | WGra | Default ramp rate of change of active power due to command or internal action.
13 |  | PFMinQ1 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ1 | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
14 |  | PFMinQ2 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ2 | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
15 |  | PFMinQ3 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ3 | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
16 |  | PFMinQ4 |  |  | int16 |  | PFMin_SF | cos() | RW |  |  | PFMinQ4 | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
17 |  | VArAct |  |  | enum16 |  |  |  | RW |  |  | VArAct | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
|  | SWITCH | 1
|  | MAINTAIN | 2
18 |  | ClcTotVA |  |  | enum16 |  |  |  | RW |  |  | ClcTotVA | Calculation method for total apparent power. 1=vector 2=arithmetic.
|  | VECTOR | 1
|  | ARITHMETIC | 2
19 |  | MaxRmpRte |  |  | uint16 |  | MaxRmpRte_SF | % WGra | RW |  |  | MaxRmpRte | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
20 |  | ECPNomHz |  |  | uint16 |  | ECPNomHz_SF | Hz | RW |  |  | ECPNomHz | Setpoint for nominal frequency at the ECP.
21 |  | ConnPh |  |  | enum16 |  |  |  | RW |  |  | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
|  | A | 1
|  | B | 2
|  | C | 3
22 |  | WMax_SF |  |  | sunssf |  |  |  |  | M |  | WMax_SF | Scale factor for real power.
23 |  | VRef_SF |  |  | sunssf |  |  |  |  | M |  | VRef_SF | Scale factor for voltage at the PCC.
24 |  | VRefOfs_SF |  |  | sunssf |  |  |  |  | M |  | VRefOfs_SF | Scale factor for offset voltage.
25 |  | VMinMax_SF |  |  | sunssf | [6 empty] | VMinMax_SF | Scale factor for min/max voltages.
26 |  | VAMax_SF |  |  | sunssf | [6 empty] | VAMax_SF | Scale factor for apparent power.
27 |  | VArMax_SF |  |  | sunssf | [6 empty] | VArMax_SF | Scale factor for reactive power.
28 |  | WGra_SF |  |  | sunssf | [6 empty] | WGra_SF | Scale factor for default ramp rate.
29 |  | PFMin_SF |  |  | sunssf | [6 empty] | PFMin_SF | Scale factor for minimum power factor.
30 |  | MaxRmpRte_SF |  |  | sunssf | [6 empty] | MaxRmpRte_SF | Scale factor for maximum ramp percentage.
31 |  | ECPNomHz_SF |  |  | sunssf | [6 empty] | ECPNomHz_SF | Scale factor for nominal frequency.

## 122 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | status |  |  | group | [6 empty] | Measurements_Status | Inverter Controls Extended Measurements and Status
0 |  | ID | 122 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | PVConn |  |  | bitfield16 |  |  |  |  | M |  | PVConn | PV inverter present/available status. Enumerated value.
|  | CONNECTED | 0
|  | AVAILABLE | 1
|  | OPERATING | 2
|  | TEST | 3
3 |  | StorConn |  |  | bitfield16 |  |  |  |  | M |  | StorConn | Storage inverter present/available status. Enumerated value.
|  | CONNECTED | 0
|  | AVAILABLE | 1
|  | OPERATING | 2
|  | TEST | 3
4 |  | ECPConn |  |  | bitfield16 |  |  |  |  | M |  | ECPConn | ECP connection status: disconnected=0 connected=1.
|  | CONNECTED | 0
5 |  | ActWh |  |  | acc64 |  |  | Wh |  |  |  | ActWh | AC lifetime active (real) energy output.
9 |  | ActVAh |  |  | acc64 |  |  | VAh |  |  |  | ActVAh | AC lifetime apparent energy output.
13 |  | ActVArhQ1 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ1 | AC lifetime reactive energy output in quadrant 1.
17 |  | ActVArhQ2 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ2 | AC lifetime reactive energy output in quadrant 2.
21 |  | ActVArhQ3 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ3 | AC lifetime negative energy output in quadrant 3.
25 |  | ActVArhQ4 |  |  | acc64 |  |  | varh |  |  |  | ActVArhQ4 | AC lifetime reactive energy output in quadrant 4.
29 |  | VArAval |  |  | int16 |  | VArAval_SF | var |  |  |  | VArAval | Amount of VARs available without impacting watts output.
30 |  | VArAval_SF |  |  | sunssf | [6 empty] | VArAval_SF | Scale factor for available VARs.
31 |  | WAval |  |  | uint16 |  | WAval_SF | var |  |  |  | WAval | Amount of Watts available.
32 |  | WAval_SF |  |  | sunssf | [6 empty] | WAval_SF | Scale factor for available Watts.
33 |  | StSetLimMsk |  |  | bitfield32 | [6 empty] | StSetLimMsk | Bit Mask indicating setpoint limit(s) reached.
|  | WMax | 0
|  | VAMax | 1
|  | VArAval | 2
|  | VArMaxQ1 | 3
|  | VArMaxQ2 | 4
|  | VArMaxQ3 | 5
|  | VArMaxQ4 | 6
|  | PFMinQ1 | 7
|  | PFMinQ2 | 8
|  | PFMinQ3 | 9
|  | PFMinQ4 | 10
35 |  | StActCtl |  |  | bitfield32 | [6 empty] | StActCtl | Bit Mask indicating which inverter controls are currently active.
|  | FixedW | 0
|  | FixedVAR | 1
|  | FixedPF | 2
|  | Volt-VAr | 3
|  | Freq-Watt-Param | 4
|  | Freq-Watt-Curve | 5
|  | Dyn-Reactive-Current | 6
|  | LVRT | 7
|  | HVRT | 8
|  | Watt-PF | 9
|  | Volt-Watt | 10
|  | Scheduled | 12
|  | LFRT | 13
|  | HFRT | 14
37 |  | TmSrc |  |  | string | 4 | [5 empty] | TmSrc | Source of time synchronization.
41 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Tms | Seconds since 01-01-2000 00:00 UTC
43 |  | RtSt |  |  | bitfield16 | [6 empty] | RtSt | Bit Mask indicating active ride-through status.
|  | LVRT_ACTIVE | 0
|  | HVRT_ACTIVE | 1
|  | LFRT_ACTIVE | 2
|  | HFRT_ACTIVE | 3
44 |  | Ris |  |  | uint16 |  | Ris_SF | ohms |  |  |  | Ris | Isolation resistance.
45 |  | Ris_SF |  |  | sunssf | [6 empty] | Ris_SF | Scale factor for isolation resistance.

## 123 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | controls |  |  | group | [6 empty] | Immediate Controls | Immediate Inverter Controls
0 |  | ID | 123 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Conn_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_WinTms | Time window for connect/disconnect.
3 |  | Conn_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | Conn_RvrtTms | Timeout period for connect/disconnect.
4 |  | Conn |  |  | enum16 |  |  |  | RW | M |  | Conn | Enumerated valued. Connection control.
|  | DISCONNECT | 0
|  | CONNECT | 1
5 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | % WMax | RW | M |  | WMaxLimPct | Set power output to specified level.
6 |  | WMaxLimPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_WinTms | Time window for power limit change.
7 |  | WMaxLimPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RvrtTms | Timeout period for power limit.
8 |  | WMaxLimPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | WMaxLimPct_RmpTms | Ramp time for moving from current setpoint to new setpoint.
9 |  | WMaxLim_Ena |  |  | enum16 |  |  |  | RW | M |  | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
10 |  | OutPFSet |  |  | int16 |  | OutPFSet_SF | cos() | RW | M |  | OutPFSet | Set power factor to specific value - cosine of angle.
11 |  | OutPFSet_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_WinTms | Time window for power factor change.
12 |  | OutPFSet_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RvrtTms | Timeout period for power factor.
13 |  | OutPFSet_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | OutPFSet_RmpTms | Ramp time for moving from current setpoint to new setpoint.
14 |  | OutPFSet_Ena |  |  | enum16 |  |  |  | RW | M |  | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
15 |  | VArWMaxPct |  |  | int16 |  | VArPct_SF | % WMax | RW |  |  | VArWMaxPct | Reactive power in percent of WMax.
16 |  | VArMaxPct |  |  | int16 |  | VArPct_SF | % VArMax | RW |  |  | VArMaxPct | Reactive power in percent of VArMax.
17 |  | VArAvalPct |  |  | int16 |  | VArPct_SF | % VArAval | RW |  |  | VArAvalPct | Reactive power in percent of VArAval.
18 |  | VArPct_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_WinTms | Time window for VAR limit change.
19 |  | VArPct_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RvrtTms | Timeout period for VAR limit.
20 |  | VArPct_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | VArPct_RmpTms | Ramp time for moving from current setpoint to new setpoint.
21 |  | VArPct_Mod |  |  | enum16 |  |  |  | RW |  |  | VArPct_Mod | Enumerated value. VAR percent limit mode.
|  | NONE | 0
|  | WMax | 1
|  | VArMax | 2
|  | VArAval | 3
22 |  | VArPct_Ena |  |  | enum16 |  |  |  | RW | M |  | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control.
|  | DISABLED | 0
|  | ENABLED | 1
23 |  | WMaxLimPct_SF |  |  | sunssf |  |  |  |  | M |  | WMaxLimPct_SF | Scale factor for power output percent.
24 |  | OutPFSet_SF |  |  | sunssf |  |  |  |  | M |  | OutPFSet_SF | Scale factor for power factor.
25 |  | VArPct_SF |  |  | sunssf | [6 empty] | VArPct_SF | Scale factor for reactive power percent.

## 124 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | storage |  |  | group | [6 empty] | Storage | Basic Storage Controls
0 |  | ID | 124 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WChaMax |  |  | uint16 |  | WChaMax_SF | W | RW | M |  | WChaMax | Setpoint for maximum charge.
3 |  | WChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WChaGra | Setpoint for maximum charging rate. Default is MaxChaRte.
4 |  | WDisChaGra |  |  | uint16 |  | WChaDisChaGra_SF | % WChaMax/sec | RW | M |  | WDisChaGra | Setpoint for maximum discharge rate. Default is MaxDisChaRte.
5 |  | StorCtl_Mod |  |  | bitfield16 |  |  |  | RW | M |  | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value.
|  | CHARGE | 0
|  | DiSCHARGE | 1
6 |  | VAChaMax |  |  | uint16 |  | VAChaMax_SF | VA | RW |  |  | VAChaMax | Setpoint for maximum charging VA.
7 |  | MinRsvPct |  |  | uint16 |  | MinRsvPct_SF | % WChaMax | RW |  |  | MinRsvPct | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
8 |  | ChaState |  |  | uint16 |  | ChaState_SF | % AhrRtg |  |  |  | ChaState | Currently available energy as a percent of the capacity rating.
9 |  | StorAval |  |  | uint16 |  | StorAval_SF | AH |  |  |  | StorAval | State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg).
10 |  | InBatV |  |  | uint16 |  | InBatV_SF | V |  |  |  | InBatV | Internal battery voltage.
11 |  | ChaSt |  |  | enum16 | [6 empty] | ChaSt | Charge status of storage device. Enumerated value.
|  | OFF | 1
|  | EMPTY | 2
|  | DISCHARGING | 3
|  | CHARGING | 4
|  | FULL | 5
|  | HOLDING | 6
|  | TESTING | 7
12 |  | OutWRte |  |  | int16 |  | InOutWRte_SF | % WDisChaMax | RW |  |  | OutWRte | Percent of max discharge rate.
13 |  | InWRte |  |  | int16 |  | InOutWRte_SF | % WChaMax | RW |  |  | InWRte | Percent of max charging rate.
14 |  | InOutWRte_WinTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_WinTms | Time window for charge/discharge rate change.
15 |  | InOutWRte_RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RvrtTms | Timeout period for charge/discharge rate.
16 |  | InOutWRte_RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | InOutWRte_RmpTms | Ramp time for moving from current setpoint to new setpoint.
17 |  | ChaGriSet |  |  | enum16 |  |  |  | RW
|  | PV | 0
|  | GRID | 1
18 |  | WChaMax_SF |  |  | sunssf |  |  |  |  | M |  | WChaMax_SF | Scale factor for maximum charge.
19 |  | WChaDisChaGra_SF |  |  | sunssf |  |  |  |  | M |  | WChaDisChaGra_SF | Scale factor for maximum charge and discharge rate.
20 |  | VAChaMax_SF |  |  | sunssf | [6 empty] | VAChaMax_SF | Scale factor for maximum charging VA.
21 |  | MinRsvPct_SF |  |  | sunssf | [6 empty] | MinRsvPct_SF | Scale factor for minimum reserve percentage.
22 |  | ChaState_SF |  |  | sunssf | [6 empty] | ChaState_SF | Scale factor for available energy percent.
23 |  | StorAval_SF |  |  | sunssf | [6 empty] | StorAval_SF | Scale factor for state of charge.
24 |  | InBatV_SF |  |  | sunssf | [6 empty] | InBatV_SF | Scale factor for battery voltage.
25 |  | InOutWRte_SF |  |  | sunssf | [6 empty] | InOutWRte_SF | Scale factor for percent charge/discharge rate.

## 125 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | pricing |  |  | group | [6 empty] | Pricing | Pricing Signal
0 |  | ID | 125 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is price-based charge/discharge mode active?
|  | ENABLE | 0
3 |  | SigType |  |  | enum16 |  |  |  | RW |  |  | SigType | Meaning of the pricing signal. When a Price schedule is used, type must match the schedule range variable description.
|  | UNKNOWN | 0
|  | ABSOLUTE | 1
|  | RELATIVE | 2
|  | MULTIPLIER | 3
|  | LEVEL | 4
4 |  | Sig |  |  | int16 |  | Sig_SF |  | RW | M |  | Sig | Utility/ESP specific pricing signal. Content depends on pricing signal type. When H/M/L type is specified. Low=0; Med=1; High=2.
5 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for charge/discharge pricing change.
6 |  | RvtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvtTms | Timeout period for charge/discharge pricing change.
7 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current charge or discharge level to new level.
8 |  | Sig_SF |  |  | sunssf |  |  |  |  | M |  | Sig_SF | Pricing signal scale factor.
9 |  | Pad |  |  | pad

## 126 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | volt_var |  |  | group | [6 empty] | Static Volt-VAR | Static Volt-VAR Arrays
0 |  | ID | 126 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Volt-VAR control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for volt-VAR change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for volt-VAR curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | The time of the PT1 in seconds (time to accomplish a change of 95%).
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
10 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M |  | DeptRef_SF | scale factor for dependent variable.
11 |  | RmpIncDec_SF |  |  | sunssf
|  | volt_var.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval.
|  | WMax | 1
|  | VArMax | 2
|  | VArAval | 3
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 Volts.
| 3 | VAr1 |  |  | int16 |  | DeptRef_SF |  | RW | M |  | VAr1 | Point 1 VARs.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 Volts.
| 5 | VAr2 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr2 | Point 2 VARs.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 2 Volts.
| 7 | VAr3 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr3 | Point 3 VARs.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 Volts.
| 9 | VAr4 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr4 | Point 4 VARs.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 Volts.
| 11 | VAr5 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr5 | Point 5 VARs.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 Volts.
| 13 | VAr6 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr6 | Point 6 VARs.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 Volts.
| 15 | VAr7 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr7 | Point 7 VARs.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 Volts.
| 17 | VAr8 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr8 | Point 8 VARs.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 Volts.
| 19 | VAr9 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr9 | Point 9 VARs.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 Volts.
| 21 | VAr10 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr10 | Point 10 VARs.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 Volts.
| 23 | VAr11 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr11 | Point 11 VARs.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 Volts.
| 25 | VAr12 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr12 | Point 12 VARs.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 Volts.
| 27 | VAr13 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr13 | Point 13 VARs.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 Volts.
| 29 | VAr14 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr14 | Point 14 VARs.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 Volts.
| 31 | VAr15 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr15 | Point 15 VARs.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 Volts.
| 33 | VAr16 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr16 | Point 16 VARs.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 Volts.
| 35 | VAr17 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr17 | Point 17 VARs.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 Volts.
| 37 | VAr18 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr18 | Point 18 VARs.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 Volts.
| 39 | VAr19 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr19 | Point 19 VARs.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 Volts.
| 41 | VAr20 |  |  | int16 |  | DeptRef_SF |  | RW |  |  | VAr20 | Point 20 VARs.
| 42 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve. (Max 16 chars)
| 50 | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 51 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % ref_value/min | RW |  |  | RmpDecTmm | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
| 52 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % ref_value/min | RW |  |  | RmpIncTmm | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
| 53 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Boolean flag indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 127 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | freq_watt_param |  |  | group | [6 empty] | Freq-Watt Param | Parameterized Frequency-Watt
0 |  | ID | 127 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | WGra |  |  | uint16 |  | WGra_SF | % PM/Hz | RW | M |  | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency.
3 |  | HzStr |  |  | int16 |  | HzStrStop_SF | Hz | RW | M |  | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs.
4 |  | HzStop |  |  | int16 |  | HzStrStop_SF | Hz | RW | M |  | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed.
5 |  | HysEna |  |  | bitfield16 |  |  |  | RW | M |  | HysEna | Enable hysteresis
|  | ENABLED | 0
6 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Parameterized Frequency-Watt control active.
|  | ENABLED | 0
7 |  | HzStopWGra |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event.
8 |  | WGra_SF |  |  | sunssf | [6 empty] | WGra_SF | Scale factor for output gradient.
9 |  | HzStrStop_SF |  |  | sunssf | [6 empty] | HzStrStop_SF | Scale factor for frequency deviations.
10 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
11 |  | Pad |  |  | pad

## 128 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | reactive_current |  |  | group | [6 empty] | Dynamic Reactive Current | Dynamic Reactive Current
0 |  | ID | 128 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ArGraMod |  |  | enum16 |  |  |  | RW | M |  | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband.
|  | EDGE | 0
|  | CENTER | 1
3 |  | ArGraSag |  |  | uint16 |  | ArGra_SF | %ARtg/%dV | RW | M |  | ArGraSag | The gradient used to increase capacitive dynamic current. A value of 0 indicates no additional reactive current support.
4 |  | ArGraSwell |  |  | uint16 |  | ArGra_SF | %ARtg/%dV | RW | M |  | ArGraSwell | The gradient used to increase inductive dynamic current. A value of 0 indicates no additional reactive current support.
5 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Activate dynamic reactive current model
|  | ENABLED | 0
6 |  | FilTms |  |  | uint16 |  |  | Secs | RW |  |  | FilTms | The time window used to calculate the moving average voltage.
7 |  | DbVMin |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced.
8 |  | DbVMax |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced.
9 |  | BlkZnV |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced.
10 |  | HysBlkZnV |  |  | uint16 |  | VRefPct_SF | % VRef | RW |  |  | HysBlkZnV | Hysteresis voltage used with BlkZnV.
11 |  | BlkZnTmms |  |  | uint16 |  |  | mSecs | RW |  |  | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops.
12 |  | HoldTmms |  |  | uint16 |  |  | mSecs | RW |  |  | HoldTmms | Hold time during which reactive current support continues after the average voltage has entered the dead zone.
13 |  | ArGra_SF |  |  | sunssf |  |  |  |  | M |  | ArGra_SF | Scale factor for the gradients.
14 |  | VRefPct_SF |  |  | sunssf | [6 empty] | VRefPct_SF | Scale factor for the voltage zone and limit settings.
15 |  | Pad |  |  | pad

## 129 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lvrt |  |  | group | [6 empty] | LVRTD | LVRT Must Disconnect
0 |  | ID | 129 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | lvrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must disconnect voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must disconnect voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must disconnect voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must disconnect voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must disconnect voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must disconnect voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must disconnect voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must disconnect voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must disconnect voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must disconnect voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must disconnect voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must disconnect voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must disconnect voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must disconnect voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must disconnect voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must disconnect voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must disconnect voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must disconnect voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must disconnect voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must disconnect voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 130 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hvrt |  |  | group | [6 empty] | HVRTD | HVRT Must Disconnect
0 |  | ID | 130 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | hvrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must disconnect voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must disconnect voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must disconnect voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must disconnect voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must disconnect voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must disconnect voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must disconnect voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must disconnect voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must disconnect voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must disconnect voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must disconnect voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must disconnect voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must disconnect voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must disconnect voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must disconnect voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must disconnect voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must disconnect voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must disconnect voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must disconnect voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must disconnect voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 131 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | watt_pf |  |  | group | [6 empty] | Watt-PF | Watt-Power Factor
0 |  | ID | 131 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is watt-PF mode active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for watt-PF change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for watt-PF curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Max number of points in array.
9 |  | W_SF |  |  | sunssf |  |  |  |  | M |  | W_SF | Scale factor for percent WMax.
10 |  | PF_SF |  |  | sunssf |  |  |  |  | M |  | PF_SF | Scale factor for PF.
11 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | watt_pf.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | W1 |  |  | int16 |  | W_SF | % WMax | RW | M |  | W1 | Point 1 Watts.
| 2 | PF1 |  |  | int16 |  | PF_SF | cos() | RW | M |  | PF1 | Point 1 PF in EEI notation.
| 3 | W2 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W2 | Point 2 Watts.
| 4 | PF2 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF2 | Point 2 PF in EEI notation.
| 5 | W3 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W3 | Point 3 Watts.
| 6 | PF3 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF3 | Point 3 PF in EEI notation.
| 7 | W4 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W4 | Point 4 Watts.
| 8 | PF4 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF4 | Point 4 PF in EEI notation.
| 9 | W5 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W5 | Point 5 Watts.
| 10 | PF5 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF5 | Point 5 PF in EEI notation.
| 11 | W6 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W6 | Point 6 Watts.
| 12 | PF6 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF6 | Point 6 PF in EEI notation.
| 13 | W7 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W7 | Point 7 Watts.
| 14 | PF7 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF7 | Point 7 PF in EEI notation.
| 15 | W8 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W8 | Point 8 Watts.
| 16 | PF8 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF8 | Point 8 PF in EEI notation.
| 17 | W9 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W9 | Point 9 Watts.
| 18 | PF9 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF9 | Point 9 PF in EEI notation.
| 19 | W10 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W10 | Point 10 Watts.
| 20 | PF10 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF10 | Point 10 PF in EEI notation.
| 21 | W11 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W11 | Point 11 Watts.
| 22 | PF11 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF11 | Point 11 PF in EEI notation.
| 23 | W12 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W12 | Point 12 Watts.
| 24 | PF12 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF12 | Point 12 PF in EEI notation.
| 25 | W13 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W13 | Point 13 Watts.
| 26 | PF13 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF13 | Point 13 PF in EEI notation.
| 27 | W14 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W14 | Point 14 Watts.
| 28 | PF14 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF14 | Point 14 PF in EEI notation.
| 29 | W15 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W15 | Point 15 Watts.
| 30 | PF15 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF15 | Point 15 PF in EEI notation.
| 31 | W16 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W16 | Point 16 Watts.
| 32 | PF16 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF16 | Point 16 PF in EEI notation.
| 33 | W17 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W17 | Point 17 Watts.
| 34 | PF17 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF17 | Point 17 PF in EEI notation.
| 35 | W18 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W18 | Point 18 Watts.
| 36 | PF18 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF18 | Point 18 PF in EEI notation.
| 37 | W19 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W19 | Point 19 Watts.
| 38 | PF19 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF19 | Point 19 PF in EEI notation.
| 39 | W20 |  |  | int16 |  | W_SF | % WMax | RW |  |  | W20 | Point 20 Watts.
| 40 | PF20 |  |  | int16 |  | PF_SF | cos() | RW |  |  | PF20 | Point 20 PF in EEI notation.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | RmpPT1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPT1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 50 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % PF/min | RW |  |  | RmpDecTmm | The maximum rate at which the power factor may be reduced in response to changes in the power value.
| 51 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % PF/min | RW |  |  | RmpIncTmm | The maximum rate at which the power factor may be increased in response to changes in the power value.
| 52 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1
| 53 | Pad |  |  | pad

## 132 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | volt_watt |  |  | group | [6 empty] | Volt-Watt | Volt-Watt
0 |  | ID | 132 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is Volt-Watt control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for volt-watt change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for volt-watt curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend min. 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of points in array (maximum 20).
9 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
10 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M |  | DeptRef_SF | Scale Factor for % DeptRef
11 |  | RmpIncDec_SF |  |  | sunssf | [6 empty] | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | volt_watt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail
|  | %WMax | 1
|  | %WAval | 2
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 Volts.
| 3 | W1 |  |  | int16 |  | DeptRef_SF | % VRef | RW | M |  | W1 | Point 1 Watts.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 Volts.
| 5 | W2 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W2 | Point 2 Watts.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 Volts.
| 7 | W3 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W3 | Point 3 Watts.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 Volts.
| 9 | W4 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W4 | Point 4 Watts.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 Volts.
| 11 | W5 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W5 | Point 5 Watts.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 Volts.
| 13 | W6 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W6 | Point 6 Watts.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 Volts.
| 15 | W7 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W7 | Point 7 Watts.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 Volts.
| 17 | W8 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W8 | Point 8 Watts.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 Volts.
| 19 | W9 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W9 | Point 9 Watts.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 Volts.
| 21 | W10 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W10 | Point 10 Watts.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 Volts.
| 23 | W11 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W11 | Point 11 Watts.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 Volts.
| 25 | W12 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W12 | Point 12 Watts.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 Volts.
| 27 | W13 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W13 | Point 13 Watts.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 Volts.
| 29 | W14 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W14 | Point 14 Watts.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 Volts.
| 31 | W15 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W15 | Point 15 Watts.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 Volts.
| 33 | W16 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W16 | Point 16 Watts.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 Volts.
| 35 | W17 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W17 | Point 17 Watts.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 Volts.
| 37 | W18 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W18 | Point 18 Watts.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 Volts.
| 39 | W19 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W19 | Point 19 Watts.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 Volts.
| 41 | W20 |  |  | int16 |  | DeptRef_SF | % VRef | RW |  |  | W20 | Point 20 Watts.
| 42 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 50 | RmpPt1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPt1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 51 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpDecTmm | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
| 52 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpIncTmm | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
| 53 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 133 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | schedule |  |  | group | [6 empty] | Basic Scheduling | Basic Scheduling
0 |  | ID | 133 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActSchd |  |  | bitfield32 |  |  |  | RW | M |  | ActSchd | Bitfield of active schedules
|  | SCHED1 | 0
|  | SCHED2 | 1
|  | SCHED3 | 2
|  | SCHED4 | 3
|  | SCHED5 | 4
|  | SCHED6 | 5
|  | SCHED7 | 6
|  | SCHED8 | 7
|  | SCHED9 | 8
|  | SCHED10 | 9
|  | SCHED12 | 10
|  | SCHED13 | 11
|  | SCHED14 | 12
|  | SCHED15 | 13
|  | SCHED16 | 14
|  | SCHED17 | 15
|  | SCHED18 | 16
|  | SCHED19 | 17
|  | SCHED20 | 18
|  | SCHED21 | 19
|  | SCHED22 | 21
|  | SCHED23 | 22
|  | SCHED24 | 23
|  | SCHED25 | 24
|  | SCHED26 | 25
|  | SCHED27 | 26
|  | SCHED28 | 27
|  | SCHED29 | 28
|  | SCHED30 | 29
|  | SCHED31 | 30
|  | SCHED32 | 31
4 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is basic scheduling active.
|  | ENABLED | 0
5 |  | NSchd |  |  | uint16 |  |  |  |  | M |  | NSchd | Number of schedules supported (recommend min. 4, max 32)
6 |  | NPts |  |  | uint16 |  |  |  |  | M |  | NPts | Number of schedule entries supported (maximum of 10).
7 |  | Pad |  |  | pad | [6 empty] | Pad | Pad register.
|  | schedule.repeating |  | 0 | group
| 0 | ActPts |  |  | uint16 |  |  |  | RW | M |  | ActPts | Number of active entries in schedule.
| 1 | StrTms |  |  | uint32 |  |  | Secs | RW | M |  | StrTms | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC.
| 3 | RepPer |  |  | uint16 |  |  |  | RW | M |  | RepPer | The repetition count for time-based schedules (0=repeat forever)
| 4 | IntvTyp |  |  | enum16 |  |  |  | RW | M |  | SchdTyp | The repetition frequency for time-based schedules: no repeat=0
|  | ONETIME | 0
|  | DAILY | 1
|  | WEEKLY | 2
|  | MONTHLY | 3
|  | WEEKDAY | 4
|  | HOLIDAY | 5
|  | WEEKEND | 6
|  | YEARLY | 7
| 5 | XTyp |  |  | enum16 |  |  |  | RW | M |  | XTyp | The meaning of the X-values in the array.
|  | UNSET | 0
|  | TIME | 1
|  | TEMP | 2
|  | PRICE | 3
|  | OTHER | 99
| 6 | X_SF |  |  | sunssf |  |  |  | RW | M |  | X_SF | Scale factor for schedule range values.
| 7 | YTyp |  |  | enum16 |  |  |  | RW | M |  | YTyp | The meaning of the Y-values in the array.
|  | UNSET | 0
|  | WMax | 1
|  | RSRVD2 | 2
|  | PF | 3
|  | RSRVD4 | 4
|  | WATT_PRICE | 5
|  | VAR_PRICE | 6
|  | RSRVD7 | 7
|  | VOLT_VAR_ARRAY | 8
|  | WChaGra | 9
|  | WDisChaGra | 10
|  | VArAval | 11
|  | Schedule | 12
|  | OTHER | 99
| 8 | Y_SF |  |  | sunssf |  |  |  | RW | M |  | Y_SF | Scale factor for schedule target values.
| 9 | X1 |  |  | int32 |  | X_SF |  | RW | M |  | X1 | Entry 1 range.
| 11 | Y1 |  |  | int32 |  | Y_SF |  | RW | M |  | Y1 | Entry 1 target.
| 13 | X2 |  |  | int32 |  | X_SF |  | RW |  |  | X2 | Entry 2 range.
| 15 | Y2 |  |  | int32 |  | Y_SF |  | RW |  |  | Y2 | Entry 2 target.
| 17 | X3 |  |  | int32 |  | X_SF |  | RW |  |  | X3 | Entry 3 range.
| 19 | Y3 |  |  | int32 |  | Y_SF |  | RW |  |  | Y3 | Entry 3 target.
| 21 | X4 |  |  | int32 |  | X_SF |  | RW |  |  | X4 | Entry 4 range.
| 23 | Y4 |  |  | int32 |  | Y_SF |  | RW |  |  | Y4 | Entry 4 target.
| 25 | X5 |  |  | int32 |  | X_SF |  | RW |  |  | X5 | Entry 15range.
| 27 | Y5 |  |  | int32 |  | Y_SF |  | RW |  |  | Y5 | Entry 5 target.
| 29 | X6 |  |  | int32 |  | X_SF |  | RW |  |  | X6 | Entry 6 range.
| 31 | Y6 |  |  | int32 |  | Y_SF |  | RW |  |  | Y6 | Entry 6 target.
| 33 | X7 |  |  | int32 |  | X_SF |  | RW |  |  | X7 | Entry 7 range.
| 35 | Y7 |  |  | int32 |  | Y_SF |  | RW |  |  | Y7 | Entry 7 target.
| 37 | X8 |  |  | int32 |  | X_SF |  | RW |  |  | X8 | Entry 8 range.
| 39 | Y8 |  |  | int32 |  | Y_SF |  | RW |  |  | Y8 | Entry 8 target.
| 41 | X9 |  |  | int32 |  | X_SF |  | RW |  |  | X9 | Entry 9 range.
| 43 | Y9 |  |  | int32 |  | Y_SF |  | RW |  |  | Y9 | Entry 9 target.
| 45 | X10 |  |  | int32 |  | X_SF |  | RW |  |  | X10 | Entry 10 range.
| 47 | Y10 |  |  | int32 |  | Y_SF |  | RW |  |  | Y10 | Entry 10 target.
| 49 | Nam |  |  | string | 8 |  |  | RW |  |  | Nam | Optional description for schedule.
| 57 | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for schedule entry change.
| 58 | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current target to new target.
| 59 | ActIndx |  |  | uint16 |  |  |  |  | M |  | ActIndx | Index of active entry in the active schedule.

## 134 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | freq_watt |  |  | group | [6 empty] | Freq-Watt Crv | Curve-Based Frequency-Watt
0 |  | ID | 134 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | Is curve-based Frequency-Watt control active.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for freq-watt change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for freq-watt curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend min. 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 10).
9 |  | Hz_SF |  |  | sunssf |  |  | SF |  | M |  | Hz_SF | Scale factor for frequency.
10 |  | W_SF |  |  | sunssf |  |  | SF |  | M |  | W_SF | Scale factor for percent WRef.
11 |  | RmpIncDec_SF |  |  | sunssf |  |  | SF |  |  |  | RmpIncDec_SF | Scale factor for increment and decrement ramps.
|  | freq_watt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 Hertz.
| 2 | W1 |  |  | int16 |  | W_SF | % WRef | RW | M |  | W1 | Point 1 Watts.
| 3 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 Hertz.
| 4 | W2 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W2 | Point 2 Watts.
| 5 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 Hertz.
| 6 | W3 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W3 | Point 3 Watts.
| 7 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 Hertz.
| 8 | W4 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W4 | Point 4 Watts.
| 9 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 Hertz.
| 10 | W5 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W5 | Point 5 Watts.
| 11 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 Hertz.
| 12 | W6 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W6 | Point 6 Watts.
| 13 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 Hertz.
| 14 | W7 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W7 | Point 7 Watts.
| 15 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 Hertz.
| 16 | W8 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W8 | Point 8 Watts.
| 17 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 Hertz.
| 18 | W9 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W9 | Point 9 Watts.
| 19 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 Hertz.
| 20 | W10 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W10 | Point 10 Watts.
| 21 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 Hertz.
| 22 | W11 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W11 | Point 11 Watts.
| 23 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 Hertz.
| 24 | W12 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W12 | Point 12 Watts.
| 25 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 Hertz.
| 26 | W13 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W13 | Point 13 Watts.
| 27 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 Hertz.
| 28 | W14 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W14 | Point 14 Watts.
| 29 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 Hertz.
| 30 | W15 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W15 | Point 15 Watts.
| 31 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 Hertz.
| 32 | W16 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W16 | Point 16 Watts.
| 33 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 Hertz.
| 34 | W17 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W17 | Point 17 Watts.
| 35 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 Hertz.
| 36 | W18 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W18 | Point 18 Watts.
| 37 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 Hertz.
| 38 | W19 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W19 | Point 19 Watts.
| 39 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 Hertz.
| 40 | W20 |  |  | int16 |  | W_SF | % WRef | RW |  |  | W20 | Point 20 Watts.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve. (Max 16 chars)
| 49 | RmpPT1Tms |  |  | uint16 |  |  | Secs | RW |  |  | RmpPT1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%).
| 50 | RmpDecTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpDecTmm | The maximum rate at which the power value may be reduced in response to changes in the frequency value.
| 51 | RmpIncTmm |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpIncTmm | The maximum rate at which the power value may be increased in response to changes in the frequency value.
| 52 | RmpRsUp |  |  | uint16 |  | RmpIncDec_SF | % WMax/min | RW |  |  | RmpRsUp | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function.
| 53 | SnptW |  |  | bitfield16 |  |  |  | RW | M |  | SnptW | 1=enable snapshot/capture mode
| 54 | WRef |  |  | uint16 |  | W_SF | W | RW |  |  | WRef | Reference active power (default = WMax).
| 55 | WRefStrHz |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | WRefStrHz | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output.
| 56 | WRefStopHz |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | WRefStopHz | Frequency deviation from nominal frequency at which to release the power output.
| 57 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 135 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lfrt |  |  | group | [6 empty] | LFRT | Low Frequency Ride-through
0 |  | ID | 135 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | lfrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must disconnect frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must disconnect frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must disconnect frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must disconnect frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must disconnect frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must disconnect frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must disconnect frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must disconnect frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must disconnect frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must disconnect frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must disconnect frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must disconnect frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must disconnect frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must disconnect frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must disconnect frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must disconnect frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must disconnect frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must disconnect frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must disconnect frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must disconnect frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 136 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hfrt |  |  | group | [6 empty] | HFRT | High Frequency Ride-through
0 |  | ID | 136 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HFRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | hfrt.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must disconnect duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must disconnect frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must disconnect duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must disconnect frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must disconnect duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must disconnect frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must disconnect duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must disconnect frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must disconnect duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must disconnect frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must disconnect duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must disconnect frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must disconnect duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must disconnect frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must disconnect duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must disconnect frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must disconnect duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must disconnect frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must disconnect duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must disconnect frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must disconnect duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must disconnect frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must disconnect duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must disconnect frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must disconnect duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must disconnect frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must disconnect duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must disconnect frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must disconnect duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must disconnect frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must disconnect duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must disconnect frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must disconnect duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must disconnect frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must disconnect duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must disconnect frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must disconnect duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must disconnect frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must disconnect duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must disconnect frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 137 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lvrtc |  |  | group | [6 empty] | LVRTC | LVRT must remain connected
0 |  | ID | 137 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | lvrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must remain connected voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must remain connected voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must remain connected voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must remain connected voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must remain connected voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must remain connected voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must remain connected voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must remain connected voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must remain connected voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must remain connected voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must remain connected voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must remain connected voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must remain connected voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must remain connected voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must remain connected voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must remain connected voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must remain connected voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must remain connected voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must remain connected voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must remain connected voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 138 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hvrtc |  |  | group | [6 empty] | HVRTC | HVRT must remain connected
0 |  | ID | 138 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | HVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for HVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for HVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | Pad |  |  | pad
|  | hvrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 must remain connected voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 must remain connected voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 must remain connected voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 must remain connected voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 must remain connected voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 must remain connected voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 must remain connected voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 must remain connected voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 must remain connected voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 must remain connected voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 must remain connected voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 must remain connected voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 must remain connected voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 must remain connected voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 must remain connected voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 must remain connected voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 must remain connected voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 must remain connected voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 must remain connected voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 must remain connected voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 139 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lvrtx |  |  | group | [6 empty] | LVRTX | LVRT extended curve
0 |  | ID | 139 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | lvrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 140 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hvrtx |  |  | group | [6 empty] | HVRTX | HVRT extended curve
0 |  | ID | 140 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LVRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LVRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LVRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | V_SF |  |  | sunssf |  |  |  |  | M |  | V_SF | Scale factor for percent VRef.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | hvrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | V1 |  |  | uint16 |  | V_SF | % VRef | RW | M |  | V1 | Point 1 voltage.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | V2 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V2 | Point 2 voltage.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | V3 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V3 | Point 3 voltage.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | V4 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V4 | Point 4 voltage.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | V5 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V5 | Point 5 voltage.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | V6 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V6 | Point 6 voltage.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | V7 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V7 | Point 7 voltage.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | V8 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V8 | Point 8 voltage.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | V9 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V9 | Point 9 voltage.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | V10 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V10 | Point 10 voltage.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | V11 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V11 | Point 11 voltage.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | V12 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V12 | Point 12 voltage.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | V13 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V13 | Point 13 voltage.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | V14 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V14 | Point 14 voltage.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | V15 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V15 | Point 15 voltage.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | V16 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V16 | Point 16 voltage.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | V17 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V17 | Point 17 voltage.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | V18 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V18 | Point 18 voltage.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | V19 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V19 | Point 19 voltage.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | V20 |  |  | uint16 |  | V_SF | % VRef | RW |  |  | V20 | Point 20 voltage.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 141 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lfrtc |  |  | group | [6 empty] | LFRTC | LFRT must remain connected
0 |  | ID | 141 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | lfrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must remain connected frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must remain connected frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must remain connected frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must remain connected frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must remain connected frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must remain connected frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must remain connected frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must remain connected frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must remain connected frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must remain connected frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must remain connected frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must remain connected frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must remain connected frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must remain connected frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must remain connected frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must remain connected frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must remain connected frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must remain connected frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must remain connected frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must remain connected frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 142 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hfrtc |  |  | group | [6 empty] | HFRTC | HFRT must remain connected
0 |  | ID | 142 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | Pad |  |  | pad
|  | hfrtc.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 must remain connected duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 must remain connected frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 must remain connected duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 must remain connected frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 must remain connected duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 must remain connected frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 must remain connected duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 must remain connected frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 must remain connected duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 must remain connected frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 must remain connected duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 must remain connected frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 must remain connected duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 must remain connected frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 must remain connected duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 must remain connected frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 must remain connected duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 must remain connected frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 must remain connected duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 must remain connected frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 must remain connected duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 must remain connected frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 must remain connected duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 must remain connected frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 must remain connected duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 must remain connected frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 must remain connected duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 must remain connected frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 must remain connected duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 must remain connected frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 must remain connected duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 must remain connected frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 must remain connected duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 must remain connected frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 must remain connected duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 must remain connected frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 must remain connected duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 must remain connected frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 must remain connected duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 must remain connected frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 143 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lfrtx |  |  | group | [6 empty] | LFRTX | LFRT extended curve
0 |  | ID | 143 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | lfrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 144 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | hfrtx |  |  | group | [6 empty] | HFRTX | HFRT extended curve
0 |  | ID | 144 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ActCrv |  |  | uint16 |  |  |  | RW | M |  | ActCrv | Index of active curve. 0=no active curve.
3 |  | ModEna |  |  | bitfield16 |  |  |  | RW | M |  | ModEna | LHzRT control mode. Enable active curve. Bitfield value.
|  | ENABLED | 0
4 |  | WinTms |  |  | uint16 |  |  | Secs | RW |  |  | WinTms | Time window for LFRT change.
5 |  | RvrtTms |  |  | uint16 |  |  | Secs | RW |  |  | RvrtTms | Timeout period for LFRT curve selection.
6 |  | RmpTms |  |  | uint16 |  |  | Secs | RW |  |  | RmpTms | Ramp time for moving from current mode to new mode.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M |  | NCrv | Number of curves supported (recommend 4).
8 |  | NPt |  |  | uint16 |  |  |  |  | M |  | NPt | Number of curve points supported (maximum of 20).
9 |  | Tms_SF |  |  | sunssf |  |  |  |  | M |  | Tms_SF | Scale factor for duration.
10 |  | Hz_SF |  |  | sunssf |  |  |  |  | M |  | Hz_SF | Scale factor for frequency.
11 |  | CrvType |  |  | enum16 |  |  |  |  | M
|  | CEASE_TO_ENERGIZE | 1
|  | hfrtx.curve |  | 0 | group
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | ActPt | Number of active points in array.
| 1 | Tms1 |  |  | uint16 |  | Tms_SF | Secs | RW | M |  | Tms1 | Point 1 duration.
| 2 | Hz1 |  |  | uint16 |  | Hz_SF | Hz | RW | M |  | Hz1 | Point 1 frequency.
| 3 | Tms2 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms2 | Point 2 duration.
| 4 | Hz2 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz2 | Point 2 frequency.
| 5 | Tms3 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms3 | Point 3 duration.
| 6 | Hz3 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz3 | Point 3 frequency.
| 7 | Tms4 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms4 | Point 4 duration.
| 8 | Hz4 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz4 | Point 4 frequency.
| 9 | Tms5 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms5 | Point 5 duration.
| 10 | Hz5 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz5 | Point 5 frequency.
| 11 | Tms6 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms6 | Point 6 duration.
| 12 | Hz6 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz6 | Point 6 frequency.
| 13 | Tms7 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms7 | Point 7 duration.
| 14 | Hz7 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz7 | Point 7 frequency.
| 15 | Tms8 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms8 | Point 8 duration.
| 16 | Hz8 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz8 | Point 8 frequency.
| 17 | Tms9 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms9 | Point 9 duration.
| 18 | Hz9 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz9 | Point 9 frequency.
| 19 | Tms10 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms10 | Point 10 duration.
| 20 | Hz10 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz10 | Point 10 frequency.
| 21 | Tms11 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms11 | Point 11 duration.
| 22 | Hz11 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz11 | Point 11 frequency.
| 23 | Tms12 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms12 | Point 12 duration.
| 24 | Hz12 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz12 | Point 12 frequency.
| 25 | Tms13 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms13 | Point 13 duration.
| 26 | Hz13 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz13 | Point 13 frequency.
| 27 | Tms14 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms14 | Point 14 duration.
| 28 | Hz14 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz14 | Point 14 frequency.
| 29 | Tms15 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms15 | Point 15 duration.
| 30 | Hz15 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz15 | Point 15 frequency.
| 31 | Tms16 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms16 | Point 16 duration.
| 32 | Hz16 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz16 | Point 16 frequency.
| 33 | Tms17 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms17 | Point 17 duration.
| 34 | Hz17 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz17 | Point 17 frequency.
| 35 | Tms18 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms18 | Point 18 duration.
| 36 | Hz18 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz18 | Point 18 frequency.
| 37 | Tms19 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms19 | Point 19 duration.
| 38 | Hz19 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz19 | Point 19 frequency.
| 39 | Tms20 |  |  | uint16 |  | Tms_SF | Secs | RW |  |  | Tms20 | Point 20 duration.
| 40 | Hz20 |  |  | uint16 |  | Hz_SF | Hz | RW |  |  | Hz20 | Point 20 frequency.
| 41 | CrvNam |  |  | string | 8 |  |  | RW |  |  | CrvNam | Optional description for curve.
| 49 | ReadOnly |  |  | enum16 |  |  |  |  | M |  | ReadOnly | Enumerated value indicates if curve is read-only or can be modified.
|  | READWRITE | 0
|  | READONLY | 1

## 145 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ext_settings |  |  | group | [6 empty] | Extended Settings | Inverter controls extended settings
0 |  | ID | 145 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | NomRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Ramp Up Rate | Ramp up rate as a percentage of max current.
3 |  | NomRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | NomRmpDnRte | Ramp down rate as a percentage of max current.
4 |  | EmgRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Emergency Ramp Up Rate | Emergency ramp up rate as a percentage of max current.
5 |  | EmgRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Emergency Ramp Down Rate | Emergency ramp down rate as a percentage of max current.
6 |  | ConnRmpUpRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Connect Ramp Up Rate | Connect ramp up rate as a percentage of max current.
7 |  | ConnRmpDnRte |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Connect Ramp Down Rate | Connect ramp down rate as a percentage of max current.
8 |  | AGra |  |  | uint16 |  | Rmp_SF | Pct | RW |  |  | Default Ramp Rate | Ramp rate specified in percent of max current.
9 |  | Rmp_SF |  |  | sunssf | [6 empty] | Ramp Rate Scale Factor | Ramp Rate Scale Factor

## 160 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | mppt |  |  | group | [6 empty] | Multiple MPPT Inverter Extension Model
0 |  | ID | 160 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf | [6 empty] | Current Scale Factor
3 |  | DCV_SF |  |  | sunssf | [6 empty] | Voltage Scale Factor
4 |  | DCW_SF |  |  | sunssf | [6 empty] | Power Scale Factor
5 |  | DCWH_SF |  |  | sunssf | [6 empty] | Energy Scale Factor
6 |  | Evt |  |  | bitfield32 | [6 empty] | Global Events
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | RESERVED_16 | 16
|  | RESERVED_17 | 17
|  | RESERVED_18 | 18
|  | RESERVED_19 | 19
|  | TEST_FAILED | 20
|  | INPUT_UNDER_VOLTAGE | 21
|  | INPUT_OVER_CURRENT | 22
8 |  | N |  |  | count | [6 empty] | Number of Modules
9 |  | TmsPer |  |  | uint16 | [6 empty] | Timestamp Period
|  | mppt.module |  | 0 | group
| 0 | ID |  |  | uint16 | [6 empty] | Input ID
| 1 | IDStr |  |  | string | 8 | [5 empty] | Input ID Sting
| 9 | DCA |  |  | uint16 |  | DCA_SF | A |  |  |  | DC Current
| 10 | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | DC Voltage
| 11 | DCW |  |  | uint16 |  | DCW_SF | W |  |  |  | DC Power
| 12 | DCWH |  |  | acc32 |  | DCWH_SF | Wh |  |  |  | Lifetime Energy
| 14 | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp
| 16 | Tmp |  |  | int16 |  |  | C |  |  |  | Temperature
| 17 | DCSt |  |  | enum16 | [6 empty] | Operating State
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | RESERVED_10 | 10
| 18 | DCEvt |  |  | bitfield32 | [6 empty] | Module Events
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | CABINET_OPEN | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMP | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMP | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | RESERVED_16 | 16
|  | RESERVED_17 | 17
|  | RESERVED_18 | 18
|  | RESERVED_19 | 19
|  | TEST_FAILED | 20
|  | INPUT_UNDER_VOLTAGE | 21
|  | INPUT_OVER_CURRENT | 22

## 201 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | Meter (Single Phase)single phase (AN or AB) meter | Include this model for single phase (AN or AB) metering
0 |  | ID | 201 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PPVphAB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AB | Phase Voltage AB
13 |  | PPVphBC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PPVphCA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | Power_Failure | 2
|  | Under_Voltage | 3
|  | Low_PF | 4
|  | Over_Current | 5
|  | Over_Voltage | 6
|  | Missing_Sensor | 7
|  | OEM01 | 16
|  | OEM02 | 17
|  | OEM03 | 18
|  | OEM04 | 19
|  | OEM05 | 20
|  | OEM06 | 21
|  | OEM07 | 22
|  | OEM08 | 23
|  | OEM09 | 24
|  | OEM10 | 25
|  | OEM11 | 26
|  | OEM12 | 27
|  | OEM13 | 28
|  | OEM14 | 29
|  | OEM15 | 30

## 202 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | split single phase (ABN) meter
0 |  | ID | 202 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  |  |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 204 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | delta-connect three phase (abc) meter
0 |  | ID | 204 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 211 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | single phase (AN or AB) meter
0 |  | ID | 211 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  |  |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  |  |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  |  |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 212 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | split single phase (ABN) meter
0 |  | ID | 212 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  |  |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  |  |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  |  |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 214 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | delta-connect three phase (abc) meter
0 |  | ID | 214 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  |  |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  |  |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  |  |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  |  |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 220 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | Secure AC Meter Selected Readings | Include this model for secure metering
0 |  | ID | 220 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
4 |  | PhV |  |  | int16 |  | V_SF | V |  |  |  | Voltage | Average phase or line voltage
5 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
6 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
7 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
8 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
9 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
10 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
11 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
12 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
13 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
14 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
15 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
16 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
18 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
20 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
21 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
23 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
25 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
26 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
28 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
30 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
32 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
34 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
35 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | Power_Failure | 2
|  | Under_Voltage | 3
|  | Low_PF | 4
|  | Over_Current | 5
|  | Over_Voltage | 6
|  | Missing_Sensor | 7
|  | OEM01 | 16
|  | OEM02 | 17
|  | OEM03 | 18
|  | OEM04 | 19
|  | OEM05 | 20
|  | OEM06 | 21
|  | OEM07 | 22
|  | OEM08 | 23
|  | OEM09 | 24
|  | OEM10 | 25
|  | OEM11 | 26
|  | OEM12 | 27
|  | OEM13 | 28
|  | OEM14 | 29
|  | OEM15 | 30
37 |  | Rsrvd |  |  | pad |  |  |  |  | M
38 |  | Ts |  |  | uint32 |  |  |  |  | M |  | Timestamp | Timestamp value is the number of seconds since January 1, 2000
40 |  | Ms |  |  | uint16 |  |  |  |  | M |  | Milliseconds | Millisecond counter 0-999
41 |  | Seq |  |  | uint16 |  |  |  |  | M |  | Sequence | Sequence number of request
42 |  | Alg |  |  | enum16 |  |  |  |  | M |  | Algorithm | Algorithm used to compute the digital signature
|  | NONE | 0
|  | AES-GMAC-64 | 1
|  | ECC-256 | 2
43 |  | N |  |  | uint16 |  |  |  |  | M |  | N | Number of registers comprising the digital signature.
|  | ac_meter.repeating |  | 0 | group
| 0 | DS |  |  | uint16 |  |  |  |  | M

## 302 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | irradiance |  |  | group | [6 empty] | Irradiance Model | Include to support various irradiance measurements
0 |  | ID | 302 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | irradiance.repeating |  | 0 | group
| 0 | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
| 1 | POAI |  |  | uint16 |  |  | W/m2 |  |  |  | POAI | Plane-of-Array Irradiance
| 2 | DFI |  |  | uint16 |  |  | W/m2 |  |  |  | DFI | Diffuse Irradiance
| 3 | DNI |  |  | uint16 |  |  | W/m2 |  |  |  | DNI | Direct Normal Irradiance
| 4 | OTI |  |  | uint16 |  |  | W/m2 |  |  |  | OTI | Other Irradiance

## 303 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | bom_temp |  |  | group | [6 empty] | Back of Module Temperature Model | Include to support variable number of back of module temperature measurements
0 |  | ID | 303 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | bom_temp.temp |  | 0 | group
| 0 | TmpBOM |  |  | int16 |  | -1 | C |  | M |  | Temp | Back of module temperature measurement

## 304 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | inclinometer |  |  | group | [6 empty] | Inclinometer Model | Include to support orientation measurements
0 |  | ID | 304 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | inclinometer.incl |  | 0 | group
| 0 | Inclx |  |  | int32 |  | -2 | Degrees |  | M |  | X | X-Axis inclination
| 2 | Incly |  |  | int32 |  | -2 | Degrees |  |  |  | Y | Y-Axis inclination
| 4 | Inclz |  |  | int32 |  | -2 | Degrees |  |  |  | Z | Z-Axis inclination

## 305 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | location |  |  | group | [6 empty] | GPS | Include to support location measurements
0 |  | ID | 305 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Tm |  |  | string | 6 |  | hhmmss.sssZ |  |  |  | Tm | UTC 24 hour time stamp to millisecond hhmmss.sssZ format
8 |  | Date |  |  | string | 4 |  | YYYYMMDD |  |  |  | Date | UTC Date string YYYYMMDD format
12 |  | Loc |  |  | string | 20 |  | text |  |  |  | Location | Location string (40 chars max)
32 |  | Lat |  |  | int32 |  | -7 | Degrees |  |  |  | Lat | Latitude with seven degrees of precision
34 |  | Long |  |  | int32 |  | -7 | Degrees |  |  |  | Long | Longitude with seven degrees of precision
36 |  | Alt |  |  | int32 |  |  | meters |  |  |  | Altitude | Altitude measurement in meters

## 306 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ref_point |  |  | group | [6 empty] | Reference Point Model | Include to support a standard reference point
0 |  | ID | 306 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
3 |  | A |  |  | uint16 |  |  | W/m2 |  |  |  | Amps | Current measurement at reference point
4 |  | V |  |  | uint16 |  |  | W/m2 |  |  |  | Voltage | Voltage measurement at reference point
5 |  | Tmp |  |  | uint16 |  |  | W/m2 |  |  |  | Temperature | Temperature measurement at reference point

## 307 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | base_met |  |  | group | [6 empty] | Base Met | Base Meteorological Model
0 |  | ID | 307 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | TmpAmb |  |  | int16 |  | -1 | C |  |  |  | Ambient Temperature
3 |  | RH |  |  | int16 |  |  | Pct |  |  |  | Relative Humidity
4 |  | Pres |  |  | int16 |  |  | HPa |  |  |  | Barometric Pressure
5 |  | WndSpd |  |  | int16 |  |  | mps |  |  |  | Wind Speed
6 |  | WndDir |  |  | int16 |  |  | deg |  |  |  | Wind Direction
7 |  | Rain |  |  | int16 |  |  | mm |  |  |  | Rainfall
8 |  | Snw |  |  | int16 |  |  | mm |  |  |  | Snow Depth
9 |  | PPT |  |  | int16 | [6 empty] | Precipitation Type | Precipitation Type (WMO 4680 SYNOP code reference)
10 |  | ElecFld |  |  | int16 |  |  | Vm |  |  |  | Electric Field
11 |  | SurWet |  |  | int16 |  |  | kO |  |  |  | Surface Wetness
12 |  | SoilWet |  |  | int16 |  |  | Pct |  |  |  | Soil Wetness

## 308 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | mini_met |  |  | group | [6 empty] | Mini Met Model | Include to support a few basic measurements
0 |  | ID | 308 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | GHI |  |  | uint16 |  |  | W/m2 |  |  |  | GHI | Global Horizontal Irradiance
3 |  | TmpBOM |  |  | int16 |  | -1 | C |  |  |  | Temp | Back of module temperature measurement
4 |  | TmpAmb |  |  | int16 |  | -1 | C |  |  |  | Ambient Temperature
5 |  | WndSpd |  |  | uint16 |  |  | m/s |  |  |  | Wind Speed

## 401 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | string_combiner |  |  | group | [6 empty] | String Combiner (Current) | A basic string combiner
0 |  | ID | 401 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
6 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
11 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
12 |  | DCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
14 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
15 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
|  | string_combiner.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours

## 402 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | string_combiner |  |  | group | [6 empty] | String Combiner (Advanced) | An advanced string combiner
0 |  | ID | 402 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCW_SF |  |  | sunssf | [7 empty] | Power scale factor
6 |  | DCWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Energy scale factor
7 |  | DCAMax |  |  | uint16 |  |  | A |  |  |  | Rating | Maximum DC Current Rating
8 |  | N |  |  | count | [6 empty] | N | Number of Inputs
9 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
11 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
13 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
14 |  | DCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
16 |  | DCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
17 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
18 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | Watts | Output power
19 |  | DCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | DC Performance ratio value
20 |  | DCWh |  |  | uint32 |  | DCWh_SF | Wh |  | M |  | Watt-hours | Output energy
|  | string_combiner.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
| 5 | InDCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | uint32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours
| 8 | InDCV |  |  | uint16 |  | DCV_SF | V |  |  |  | Voltage | String Input Voltage
| 9 | InDCW |  |  | int16 |  | DCWh_SF | W |  |  |  | Watts | String Input Power
| 10 | InDCWh |  |  | uint32 |  |  | Wh |  |  |  | Watt-hours | String Input Energy
| 12 | InDCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | String Performance Ratio
| 13 | InN |  |  | uint16 | [6 empty] | N | Number of modules in this input string

## 403 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | string_combiner |  |  | group | [6 empty] | String Combiner (Current) | A basic string combiner model
0 |  | ID | 403 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
6 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
7 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
9 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
11 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
12 |  | DCAhr |  |  | acc32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
14 |  | DCV |  |  | int16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
15 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
16 |  | InDCA_SF |  |  | sunssf | [7 empty] | Current scale factor for inputs
17 |  | InDCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor for inputs
|  | string_combiner.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | InDCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | acc32 |  | InDCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours

## 404 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | string_combiner |  |  | group | [6 empty] | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements
0 |  | ID | 404 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DCA_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
3 |  | DCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor
4 |  | DCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor
5 |  | DCW_SF |  |  | sunssf | [7 empty] | Power scale factor
6 |  | DCWh_SF |  |  | sunssf | [7 empty] | Energy scale factor
7 |  | DCAMax |  |  | uint16 |  | DCA_SF | A |  | M |  | Rating | Maximum DC Current Rating
8 |  | N |  |  | count |  |  |  |  | M |  | N | Number of Inputs
9 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Event | Bitmask value. Events
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
11 |  | EvtVnd |  |  | bitfield32 | [6 empty] | Vendor Event | Bitmask value. Vendor defined events
13 |  | DCA |  |  | int16 |  | DCA_SF | A |  | M |  | Amps | Total measured current
14 |  | DCAhr |  |  | acc32 |  | DCAhr_SF | Ah |  |  |  | Amp-hours | Total metered Amp-hours
16 |  | DCV |  |  | int16 |  | DCV_SF | V |  |  |  | Voltage | Output Voltage
17 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Internal operating temperature
18 |  | DCW |  |  | int16 |  | DCW_SF | W |  |  |  | Watts | Output power
19 |  | DCPR |  |  | int16 |  |  | Pct |  |  |  | PR | DC Performance ratio value
20 |  | DCWh |  |  | acc32 |  | DCWh_SF | Wh |  |  |  | Watt-hours | Output energy
22 |  | InDCA_SF |  |  | sunssf | [7 empty] | Current scale factor for inputs
23 |  | InDCAhr_SF |  |  | sunssf | [7 empty] | Amp-hour scale factor for inputs
24 |  | InDCV_SF |  |  | sunssf | [7 empty] | Voltage scale factor for inputs
25 |  | InDCW_SF |  |  | sunssf | [7 empty] | Power scale factor for inputs
26 |  | InDCWh_SF |  |  | sunssf | [7 empty] | Energy scale factor for inputs
|  | string_combiner.string |  | 0 | group
| 0 | InID |  |  | uint16 |  |  |  |  | M |  | ID | Uniquely identifies this input set
| 1 | InEvt |  |  | bitfield32 |  |  |  |  | M |  | Input Event | String Input Event Flags
|  | LOW_VOLTAGE | 0
|  | LOW_POWER | 1
|  | LOW_EFFICIENCY | 2
|  | CURRENT | 3
|  | VOLTAGE | 4
|  | POWER | 5
|  | PR | 6
|  | DISCONNECTED | 7
|  | FUSE_FAULT | 8
|  | COMBINER_FUSE_FAULT | 9
|  | COMBINER_CABINET_OPEN | 10
|  | TEMP | 11
|  | GROUNDFAULT | 12
|  | REVERSED_POLARITY | 13
|  | INCOMPATIBLE | 14
|  | COMM_ERROR | 15
|  | INTERNAL_ERROR | 16
|  | THEFT | 17
|  | ARC_DETECTED | 18
| 3 | InEvtVnd |  |  | bitfield32 | [6 empty] | Input Event Vendor | String Input Vendor Event Flags
| 5 | InDCA |  |  | int16 |  | InDCA_SF | A |  | M |  | Amps | String Input Current
| 6 | InDCAhr |  |  | acc32 |  | InDCAhr_SF | Ah |  |  |  | Amp-hours | String Input Amp-Hours
| 8 | InDCV |  |  | int16 |  | InDCV_SF | V |  |  |  | Voltage | String Input Voltage
| 9 | InDCW |  |  | int16 |  | InDCW_SF | W |  |  |  | Watts | String Input Power
| 10 | InDCWh |  |  | acc32 |  | InDCWh_SF | Wh |  |  |  | Watt-hours | String Input Energy
| 12 | InDCPR |  |  | uint16 |  |  | Pct |  |  |  | PR | String Performance Ratio
| 13 | InN |  |  | uint16 | [6 empty] | N | Number of modules in this input string

## 501 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | solar_module |  |  | group | [6 empty] | Solar Module | A solar module model supporting DC-DC converter
0 |  | ID | 501 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Stat |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated value. Module Status Code
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | OTHER | 10
3 |  | StatVend |  |  | enum16 | [6 empty] | Vendor Status | Module Vendor Status Code
4 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Bitmask value. Module Event Flags
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
6 |  | EvtVend |  |  | bitfield32 | [6 empty] | Vendor Module Event Flags | Vendor specific flags
8 |  | Ctl |  |  | enum16 |  |  |  | RW |  |  | Control | Module Control
9 |  | CtlVend |  |  | enum32 |  |  |  | RW |  |  | Vendor Control | Vendor Module Control
11 |  | CtlVal |  |  | int32 |  |  |  | RW |  |  | Control Value | Module Control Value
13 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp | Time in seconds since 2000 epoch
15 |  | OutA |  |  | float32 |  |  | A |  |  |  | Output Current | Output Current
17 |  | OutV |  |  | float32 |  |  | V |  |  |  | Output Voltage | Output Voltage
19 |  | OutWh |  |  | float32 |  |  | Wh |  |  |  | Output Energy | Output Energy
21 |  | OutW |  |  | float32 |  |  | W |  |  |  | Output Power | Output Power
23 |  | Tmp |  |  | float32 |  |  | C |  |  |  | Temp | Module Temperature
25 |  | InA |  |  | float32 |  |  | A |  |  |  | Input Current | Input Current
27 |  | InV |  |  | float32 |  |  | V |  |  |  | Input Voltage | Input Voltage
29 |  | InWh |  |  | float32 |  |  | Wh |  |  |  | Input Energy | Input Energy
31 |  | InW |  |  | float32 |  |  | W |  |  |  | Input Power | Input Power

## 502 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | solar_module |  |  | group | [6 empty] | Solar Module | A solar module model supporting DC-DC converter
0 |  | ID | 502 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A_SF |  |  | sunssf | [7 empty] | Current scale factor
3 |  | V_SF |  |  | sunssf | [7 empty] | Voltage scale factor
4 |  | W_SF |  |  | sunssf | [7 empty] | Power scale factor
5 |  | Wh_SF |  |  | sunssf | [7 empty] | Energy scale factor
6 |  | Stat |  |  | enum16 |  |  |  |  | M |  | Status | Enumerated value. Module Status Code
|  | OFF | 1
|  | SLEEPING | 2
|  | STARTING | 3
|  | MPPT | 4
|  | THROTTLED | 5
|  | SHUTTING_DOWN | 6
|  | FAULT | 7
|  | STANDBY | 8
|  | TEST | 9
|  | OTHER | 10
7 |  | StatVend |  |  | enum16 | [6 empty] | Vendor Status | Module Vendor Status Code
8 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Bitmask value. Module Event Flags
|  | GROUND_FAULT | 0
|  | INPUT_OVER_VOLTAGE | 1
|  | RESERVED_2 | 2
|  | DC_DISCONNECT | 3
|  | RESERVED_4 | 4
|  | RESERVED_5 | 5
|  | MANUAL_SHUTDOWN | 6
|  | OVER_TEMPERATURE | 7
|  | RESERVED_8 | 8
|  | RESERVED_9 | 9
|  | RESERVED_10 | 10
|  | RESERVED_11 | 11
|  | BLOWN_FUSE | 12
|  | UNDER_TEMPERATURE | 13
|  | MEMORY_LOSS | 14
|  | ARC_DETECTION | 15
|  | THEFT_DETECTION | 16
|  | OUTPUT_OVER_CURRENT | 17
|  | OUTPUT_OVER_VOLTAGE | 18
|  | OUTPUT_UNDER_VOLTAGE | 19
|  | TEST_FAILED | 20
10 |  | EvtVend |  |  | bitfield32 | [6 empty] | Vendor Module Event Flags | Vendor specific flags
12 |  | Ctl |  |  | enum16 |  |  |  | RW |  |  | Control | Module Control
13 |  | CtlVend |  |  | enum32 |  |  |  | RW |  |  | Vendor Control | Vendor Module Control
15 |  | CtlVal |  |  | int32 |  |  |  | RW |  |  | Control Value | Module Control Value
17 |  | Tms |  |  | uint32 |  |  | Secs |  |  |  | Timestamp | Time in seconds since 2000 epoch
19 |  | OutA |  |  | int16 |  | A_SF | A |  |  |  | Output Current | Output Current
20 |  | OutV |  |  | int16 |  | V_SF | V |  |  |  | Output Voltage | Output Voltage
21 |  | OutWh |  |  | acc32 |  | Wh_SF | Wh |  |  |  | Output Energy | Output Energy
23 |  | OutPw |  |  | int16 |  | W_SF | W |  |  |  | Output Power | Output Power
24 |  | Tmp |  |  | int16 |  |  | C |  |  |  | Temp | Module Temperature
25 |  | InA |  |  | int16 |  | A_SF | A |  |  |  | Input Current | Input Current
26 |  | InV |  |  | int16 |  | V_SF | V |  |  |  | Input Voltage | Input Voltage
27 |  | InWh |  |  | acc32 |  | Wh_SF | Wh |  |  |  | Input Energy | Input Energy
29 |  | InW |  |  | int16 |  | W_SF | W |  |  |  | Input Power | Input Power

## 601 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | tracker_controller |  |  | group | [6 empty] | Tracker Controller DRAFT 2 | Monitors and controls multiple trackers
0 |  | ID | 601 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Nam |  |  | string | 8 | [5 empty] | Controller | Descriptive name for this control unit
10 |  | Typ |  |  | enum16 |  |  |  |  | M |  | Type | Type of tracker
|  | Unknown | 0
|  | Fixed | 1
|  | Horizontal | 2
|  | Tilted | 3
|  | Azimuth | 4
|  | Dual | 5
|  | Other | 99
11 |  | DtLoc |  |  | string | 5 |  | YYYYMMDD |  |  |  | Date | Local date in YYYYMMDD format
16 |  | TmLoc |  |  | string | 3 |  | hhmmss |  |  |  | Time | 24 hour local time stamp to second
19 |  | Day |  |  | uint16 | [6 empty] | Day | Number of the day in the year (1-366)
20 |  | GlblElCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Elevation | Global manual override target position of elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
22 |  | GlblAzCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Azimuth | Global manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
24 |  | GlblCtl |  |  | enum16 |  |  |  | RW |  |  | Global Mode | Global Control register operates on all trackers. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
|  | Automatic | 0
|  | Manual | 1
|  | Calibrate | 2
25 |  | GlblAlm |  |  | bitfield16 | [6 empty] | Global Alarm | Global tracker alarm conditions
|  | SetPoint | 0
|  | ObsEl | 1
|  | ObsAz | 2
26 |  | Dgr_SF |  |  | sunssf |  |  |  |  | M |  | SF | Scale Factor for targets and position measurements in degrees
27 |  | N |  |  | uint16 |  |  |  |  | M |  | Trackers | Number of trackers being controlled. Size of repeating block.
|  | tracker_controller.tracker |  | 0 | group
| 0 | Id |  |  | string | 8 | [5 empty] | Tracker | Descriptive name for this tracker unit
| 8 | ElTrgt |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Target Elevation | Auto target elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 10 | AzTrgt |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Target Azimuth | Auto target azimuth in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
| 12 | ElPos |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Elevation | Actual elevation position in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 14 | AzPos |  |  | int32 |  | Dgr_SF | Degrees |  |  |  | Azimuth | Actual azimuth position in degrees from true north towards east. Unimplemented for single axis horizontal tracker type
| 16 | ElCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Elevation | Manual override target position of elevation in degrees from horizontal. Unimplemented for single axis azimuth tracker type
| 18 | AzCtl |  |  | int32 |  | Dgr_SF | Degrees | RW |  |  | Manual Azimuth | Manual override target position of azimuth in degrees from true north towards east. Unimplemented for single axis azimuth tracker type
| 20 | Ctl |  |  | enum16 |  |  |  | RW |  |  | Mode | Control register. Normal operation is automatic. Operator can override the position by setting the ElCtl, AzCtl and enabling Manual operation. Entering calibration mode will revert to automatic operation after calibration is complete.
|  | Automatic | 0
|  | Manual | 1
|  | Calibrate | 2
| 21 | Alm |  |  | bitfield16 | [6 empty] | Alarm | Tracker alarm conditions
|  | SetPoint | 0
|  | ObsEl | 1
|  | ObsAz | 2

## 701
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERMeasureAC |  |  | group | [6 empty] | DER AC Measurement | DER AC measurement model.
0 |  | ID | 701 |  | uint16 |  |  |  |  | M | S | Model ID | DER AC measurement model ID. |  |  |  | 9C86 | 40070
1 |  | L | 153 |  | uint16 |  |  |  |  | M | S | Model Length | DER AC measurement model length. |  |  |  | 9C87 | 40071
Wiring Type
2 |  | ACType |  |  | enum16 |  |  |  |  | M |  | AC Wiring Type | AC wiring type. |  |  |  | 9C88 | 40072
|  | SINGLE_PHASE | 0 | [8 empty] | Single Phase
|  | SPLIT_PHASE | 1 | [8 empty] | Split Phase
|  | THREE_PHASE | 2 | [8 empty] | Three Phase
Operating State
3 |  | St |  |  | enum16 | [6 empty] | Operating State | Operating state of the DER. |  |  |  | 9C89 | 40073
|  | OFF | 0 | [8 empty] | Off
|  | ON | 1 | [8 empty] | On
Inverter State
4 |  | InvSt |  |  | enum16 | [6 empty] | Inverter State | Enumerated value. Inverter state. |  |  |  | 9C8A | 40074
|  | OFF | 0
|  | SLEEPING | 1
|  | STARTING | 2
|  | RUNNING | 3
|  | THROTTLED | 4
|  | SHUTTING_DOWN | 5
|  | FAULT | 6
|  | STANDBY | 7
Grid Connection State
5 |  | ConnSt |  |  | enum16 | [6 empty] | Grid Connection State | Grid connection state of the DER. |  |  |  | 9C8B | 40075
|  | DISCONNECTED | 0 | [8 empty] | Disconnected | Disconnected from the grid.
|  | CONNECTED | 1 | [8 empty] | Connected | Connected to the grid.
Alarms
6 |  | Alrm |  |  | bitfield32 | [6 empty] | Alarm Bitfield | Active alarms for the DER. |  |  |  | 9C8C | 40076
|  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
|  | DC_OVER_VOLT | 1 | [8 empty] | DC Over Voltage
|  | AC_DISCONNECT | 2 | [8 empty] | AC Disconnect Open
|  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect Open
|  | GRID_DISCONNECT | 4 | [8 empty] | Grid Disconnect
|  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
|  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
|  | OVER_TEMP | 7 | [8 empty] | Over Temperature
|  | OVER_FREQUENCY | 8 | [8 empty] | Frequency Above Limit
|  | UNDER_FREQUENCY | 9 | [8 empty] | Frequency Under Limit
|  | AC_OVER_VOLT | 10 | [8 empty] | AC Voltage Above Limit
|  | AC_UNDER_VOLT | 11 | [8 empty] | AC Voltage Under Limit
|  | BLOWN_STRING_FUSE | 12 | [8 empty] | Blown String Fuse On Input
|  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
|  | MEMORY_LOSS | 14 | [8 empty] | Generic Memory Or Communication Error (Internal)
|  | HW_TEST_FAILURE | 15 | [8 empty] | Hardware Test Failure
|  | MANUFACTURER_ALRM | 16 | [8 empty] | Manufacturer Alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
8 |  | DERMode |  |  | bitfield32 | [6 empty] | DER Operational Characteristics | Current operational characteristics of the DER. |  |  |  | 9C8E | 40078
|  | GRID_FOLLOWING | 0 | [8 empty] | Grid Following | The DER is operating as part of a larger grid.
|  | GRID_FORMING | 1 | [8 empty] | Grid Forming | The DER is providing the grid.
|  | PV_CLIPPED | 2 | [8 empty] | PV Output Clipped | The PV output is clipped.
Summary
10 |  | W |  |  | int16 |  | W_SF | W |  |  |  | Active Power | Total active power. Active power is positive for DER generation and negative for absorption. |  |  |  | 9C90 | 40080
11 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | Apparent Power | Total apparent power. |  |  |  | 9C91 | 40081
12 |  | Var |  |  | int16 |  | Var_SF | Var |  |  |  | Reactive Power | Total reactive power. |  |  |  | 9C92 | 40082
13 |  | PF |  |  | int16 |  | PF_SF |  |  |  |  | Power Factor | Power factor. The sign of power factor should be the sign of active power. |  |  |  | 9C93 | 40083
14 |  | A |  |  | int16 |  | A_SF | A |  |  |  | Total AC Current | Total AC current. |  |  |  | 9C94 | 40084
15 |  | LLV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LL | Line to line AC voltage as an average of active phases. |  |  |  | 9C95 | 40085
16 |  | LNV |  |  | uint16 |  | V_SF | V |  |  |  | Voltage LN | Line to neutral AC voltage as an average of active phases. |  |  |  | 9C96 | 40086
17 |  | Hz |  |  | uint32 |  | Hz_SF | Hz |  |  |  | Frequency | AC frequency. |  |  |  | 9C97 | 40087
19 |  | TotWhInj |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4). |  |  |  | 9C99 | 40089
23 |  | TotWhAbs |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3). |  |  |  | 9C9D | 40093
27 |  | TotVarhInj |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2). |  |  |  | 9CA1 | 40097
31 |  | TotVarhAbs |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4). |  |  |  | 9CA5 | 40101
Temperatures
35 |  | TmpAmb |  |  | int16 |  | Tmp_SF | C |  |  |  | Ambient Temperature | Ambient temperature. |  |  |  | 9CA9 | 40105
36 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  |  |  | Cabinet Temperature | Cabinet temperature. |  |  |  | 9CAA | 40106
37 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat sink temperature. |  |  |  | 9CAB | 40107
38 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer temperature. |  |  |  | 9CAC | 40108
39 |  | TmpSw |  |  | int16 |  | Tmp_SF | C |  |  |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature. |  |  |  | 9CAD | 40109
40 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other temperature. |  |  |  | 9CAE | 40110
L1
41 |  | WL1 |  |  | int16 |  | W_SF | W |  |  |  | Watts L1 | Active power L1. |  |  |  | 9CAF | 40111
42 |  | VAL1 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L1 | Apparent power L1. |  |  |  | 9CB0 | 40112
43 |  | VarL1 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L1 | Reactive power L1. |  |  |  | 9CB1 | 40113
44 |  | PFL1 |  |  | int16 |  | PF_SF |  |  |  |  | PF L1 | Power factor phase L1. |  |  |  | 9CB2 | 40114
45 |  | AL1 |  |  | int16 |  | A_SF | A |  |  |  | Amps L1 | Current phase L1. |  |  |  | 9CB3 | 40115
46 |  | VL1L2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-L2 | Phase voltage L1-L2. |  |  |  | 9CB4 | 40116
47 |  | VL1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L1-N | Phase voltage L1-N. |  |  |  | 9CB5 | 40117
48 |  | TotWhInjL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L1 | Total active energy injected L1. |  |  |  | 9CB6 | 40118
52 |  | TotWhAbsL1 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L1 | Total active energy absorbed L1. |  |  |  | 9CBA | 40122
56 |  | TotVarhInjL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L1 | Total reactive energy injected L1. |  |  |  | 9CBE | 40126
60 |  | TotVarhAbsL1 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L1 | Total reactive energy absorbed L1. |  |  |  | 9CC2 | 40130
L2
64 |  | WL2 |  |  | int16 |  | W_SF | W |  |  |  | Watts L2 | Active power L2. |  |  |  | 9CC6 | 40134
65 |  | VAL2 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L2 | Apparent power L2. |  |  |  | 9CC7 | 40135
66 |  | VarL2 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L2 | Reactive power L2. |  |  |  | 9CC8 | 40136
67 |  | PFL2 |  |  | int16 |  | PF_SF |  |  |  |  | PF L2 | Power factor L2. |  |  |  | 9CC9 | 40137
68 |  | AL2 |  |  | int16 |  | A_SF | A |  |  |  | Amps L2 | Current L2. |  |  |  | 9CCA | 40138
69 |  | VL2L3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-L3 | Phase voltage L2-L3. |  |  |  | 9CCB | 40139
70 |  | VL2 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L2-N | Phase voltage L2-N. |  |  |  | 9CCC | 40140
71 |  | TotWhInjL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L2 | Total active energy injected L2. |  |  |  | 9CCD | 40141
75 |  | TotWhAbsL2 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L2 | Total active energy absorbed L2. |  |  |  | 9CD1 | 40145
79 |  | TotVarhInjL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L2 | Total reactive energy injected L2. |  |  |  | 9CD5 | 40149
83 |  | TotVarhAbsL2 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L2 | Total reactive energy absorbed L2. |  |  |  | 9CD9 | 40153
L3
87 |  | WL3 |  |  | int16 |  | W_SF | W |  |  |  | Watts L3 | Active power L3. |  |  |  | 9CDD | 40157
88 |  | VAL3 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L3 | Apparent power L3. |  |  |  | 9CDE | 40158
89 |  | VarL3 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L3 | Reactive power L3. |  |  |  | 9CDF | 40159
90 |  | PFL3 |  |  | int16 |  | PF_SF |  |  |  |  | PF L3 | Power factor L3. |  |  |  | 9CE0 | 40160
91 |  | AL3 |  |  | int16 |  | A_SF | A |  |  |  | Amps L3 | Current L3. |  |  |  | 9CE1 | 40161
92 |  | VL3L1 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-L1 | Phase voltage L3-L1. |  |  |  | 9CE2 | 40162
93 |  | VL3 |  |  | uint16 |  | V_SF | V |  |  |  | Phase Voltage L3-N | Phase voltage L3-N. |  |  |  | 9CE3 | 40163
94 |  | TotWhInjL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Inj L3 | Total active energy injected L3. |  |  |  | 9CE4 | 40164
98 |  | TotWhAbsL3 |  |  | uint64 |  | TotWh_SF | Wh |  |  |  | Total Watt-Hours Abs L3 | Total active energy absorbed L3. |  |  |  | 9CE8 | 40168
102 |  | TotVarhInjL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Inj L3 | Total reactive energy injected L3. |  |  |  | 9CEC | 40172
106 |  | TotVarhAbsL3 |  |  | uint64 |  | TotVarh_SF | Varh |  |  |  | Total Var-Hours Abs L3 | Total reactive energy absorbed L3. |  |  |  | 9CF0 | 40176
Active Power Throttling
110 |  | ThrotPct |  |  | uint16 |  |  | Pct |  |  |  | Throttling In Pct | Throttling in pct of maximum active power. |  |  |  | 9CF4 | 40180
111 |  | ThrotSrc |  |  | bitfield32 | [6 empty] | Throttle Source Information | Active throttling source. |  |  |  | 9CF5 | 40181
|  | MAX_W | 0
|  | FIXED_W | 1
|  | FIXED_VAR | 2
|  | FIXED_PF | 3
|  | VOLT_VAR | 4
|  | FREQ_WATT | 5
|  | DYN_REACT_CURR | 6
|  | LVRT | 7
|  | HVRT | 8
|  | WATT_VAR | 9
|  | VOLT_WATT | 10
|  | SCHEDULED | 11
|  | LFRT | 12
|  | HFRT | 13
|  | DERATED | 14
Scale Factors
113 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor. |  |  |  | 9CF7 | 40183
114 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor. |  |  |  | 9CF8 | 40184
115 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor. |  |  |  | 9CF9 | 40185
116 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor. |  |  |  | 9CFA | 40186
117 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor. |  |  |  | 9CFB | 40187
118 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor. |  |  |  | 9CFC | 40188
119 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor. |  |  |  | 9CFD | 40189
120 |  | TotWh_SF |  |  | sunssf | [5 empty] | S | Active Energy Scale Factor | Active energy scale factor. |  |  |  | 9CFE | 40190
121 |  | TotVarh_SF |  |  | sunssf | [5 empty] | S | Reactive Energy Scale Factor | Reactive energy scale factor. |  |  |  | 9CFF | 40191
122 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature scale factor. |  |  |  | 9D00 | 40192
Manufacturer Alarm Information
123 |  | MnAlrmInfo |  |  | string | 32 | [5 empty] | Manufacturer Alarm Info | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active. |  |  |  | 9D01 | 40193

## 702
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERCapacity |  |  | group | [6 empty] | DER Capacity | DER capacity model.
0 |  | ID | 702 |  | uint16 |  |  |  |  | M | S | Model ID | DER capacity model ID. |  |  |  | 9D21 | 40225
1 |  | L | 50 |  | uint16 |  |  |  |  | M | S | Model Length | DER capacity model length. |  |  |  | 9D22 | 40226
Nameplate Ratings - Specifies capacity ratings
2 |  | WMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power Max Rating | Maximum active power rating at unity power factor in watts. |  |  |  | 9D23 | 40227
3 |  | WOvrExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Over-Excited) Rating | Active power rating at specified over-excited power factor in watts. |  |  |  | 9D24 | 40228
4 |  | WOvrExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Over-Excited PF | Specified over-excited power factor. |  |  |  | 9D25 | 40229
5 |  | WUndExtRtg |  |  | uint16 |  | W_SF | W |  |  | S | Active Power (Under-Excited) Rating | Active power rating at specified under-excited power factor in watts. |  |  |  | 9D26 | 40230
6 |  | WUndExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  | S | Specified Under-Excited PF | Specified under-excited power factor. |  |  |  | 9D27 | 40231
7 |  | VAMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Apparent Power Max Rating | Maximum apparent power rating in voltamperes. |  |  |  | 9D28 | 40232
8 |  | VarMaxInjRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Injected Rating | Maximum injected reactive power rating in vars. |  |  |  | 9D29 | 40233
9 |  | VarMaxAbsRtg |  |  | uint16 |  | Var_SF | Var |  |  | S | Reactive Power Absorbed Rating | Maximum absorbed reactive power rating in vars. |  |  |  | 9D2A | 40234
10 |  | WChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Charge Rate Max Rating | Maximum active power charge rate in watts. |  |  |  | 9D2B | 40235
11 |  | WDisChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  | S | Discharge Rate Max Rating | Maximum active power discharge rate in watts. |  |  |  | 9D2C | 40236
12 |  | VAChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Charge Rate Max VA Rating | Maximum apparent power charge rate in voltamperes. |  |  |  | 9D2D | 40237
13 |  | VADisChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  | S | Discharge Rate Max VA Rating | Maximum apparent power discharge rate in voltamperes. |  |  |  | 9D2E | 40238
14 |  | VNomRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Nominal Rating | AC voltage nominal rating. |  |  |  | 9D2F | 40239
15 |  | VMaxRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Max Rating | AC voltage maximum rating. |  |  |  | 9D30 | 40240
16 |  | VMinRtg |  |  | uint16 |  | V_SF | V |  |  | S | AC Voltage Min Rating | AC voltage minimum rating. |  |  |  | 9D31 | 40241
17 |  | AMaxRtg |  |  | uint16 |  | A_SF | A |  |  | S | AC Current Max Rating | AC current maximum rating in amps. |  |  |  | 9D32 | 40242
18 |  | PFOvrExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Over-Excited Rating | Power factor over-excited rating. |  |  |  | 9D33 | 40243
19 |  | PFUndExtRtg |  |  | uint16 |  | PF_SF |  |  |  | S | PF Under-Excited Rating | Power factor under-excited rating. |  |  |  | 9D34 | 40244
20 |  | ReactSusceptRtg |  |  | uint16 |  | S_SF | S |  |  | S | Reactive Susceptance | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state. |  |  |  | 9D35 | 40245
21 |  | NorOpCatRtg |  |  | enum16 | [5 empty] | S | Normal Operating Category | Normal operating performance category as specified in IEEE 1547-2018. |  |  |  | 9D36 | 40246
|  | CAT_A | 0 | [8 empty] | Category A
|  | CAT_B | 1 | [8 empty] | Category B
22 |  | AbnOpCatRtg |  |  | enum16 | [5 empty] | S | Abnormal Operating Category | Abnormal operating performance category as specified in IEEE 1547-2018. |  |  |  | 9D37 | 40247
|  | CAT_1 | 0 | [8 empty] | Category I
|  | CAT_2 | 1 | [8 empty] | Category II
|  | CAT_3 | 2 | [8 empty] | Category III
23 |  | CtrlModes |  |  | bitfield32 | [5 empty] | S | Supported Control Modes | Supported control mode functions. |  |  |  | 9D38 | 40248
|  | MAX_W | 0 | [8 empty] | Limit Maximum Active Power
|  | FIXED_W | 1 | [8 empty] | Fixed Active Power
|  | FIXED_VAR | 2 | [8 empty] | Fixed Reactive Power
|  | FIXED_PF | 3 | [8 empty] | Fixed Power Factor
|  | VOLT_VAR | 4 | [8 empty] | Volt-Var Function
|  | FREQ_WATT | 5 | [8 empty] | Freq-Watt Function
|  | DYN_REACT_CURR | 6 | [8 empty] | Dynamic Reactive Current Function
|  | LV_TRIP | 7 | [8 empty] | Low-Voltage Trip
|  | HV_TRIP | 8 | [8 empty] | High-Voltage Trip
|  | WATT_VAR | 9 | [8 empty] | Watt-Var Function
|  | VOLT_WATT | 10 | [8 empty] | Volt-Watt Function
|  | SCHEDULED | 11 | [8 empty] | Scheduling
|  | LF_TRIP | 12 | [8 empty] | Low-Frequency Trip
|  | HF_TRIP | 13 | [8 empty] | High-Frequency Trip
25 |  | IntIslandCatRtg |  |  | bitfield16 | [5 empty] | S | Intentional Island Categories | Intentional island categories. |  |  |  | 9D3A | 40250
|  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
|  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
|  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
|  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
Settings - Used to adjust nameplate ratings
26 |  | WMax |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power Max Setting | Maximum active power setting used to adjust maximum active power setting. |  |  |  | 9D3B | 40251
27 |  | WMaxOvrExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Over-Excited) Setting | Active power setting at specified over-excited power factor in watts. |  |  |  | 9D3C | 40252
28 |  | WOvrExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Over-Excited PF | Specified over-excited power factor. |  |  |  | 9D3D | 40253
29 |  | WMaxUndExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Under-Excited) Setting | Active power setting at specified under-excited power factor in watts. |  |  |  | 9D3E | 40254
30 |  | WUndExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Under-Excited PF | Specified under-excited power factor. |  |  |  | 9D3F | 40255
31 |  | VAMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Apparent Power Max Setting | Maximum apparent power setting used to adjust maximum apparent power rating. |  |  |  | 9D40 | 40256
32 |  | VarMaxInj |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Injected Setting | Maximum injected reactive power setting used to adjust maximum injected reactive power rating. |  |  |  | 9D41 | 40257
33 |  | VarMaxAbs |  |  | uint16 |  | Var_SF | Var | RW |  |  | Reactive Power Absorbed Setting | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating. |  |  |  | 9D42 | 40258
34 |  | WChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Charge Rate Max Setting | Maximum active power charge rate setting used to adjust maximum active power charge rate rating. |  |  |  | 9D43 | 40259
35 |  | WDisChaRteMax |  |  | uint16 |  | W_SF | W | RW |  |  | Discharge Rate Max Setting | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating. |  |  |  | 9D44 | 40260
36 |  | VAChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Charge Rate Max VA Setting | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating. |  |  |  | 9D45 | 40261
37 |  | VADisChaRteMax |  |  | uint16 |  | VA_SF | VA | RW |  |  | Discharge Rate Max VA Setting | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating. |  |  |  | 9D46 | 40262
38 |  | VNom |  |  | uint16 |  | V_SF | V | RW |  |  | Nominal AC Voltage Setting | Nominal AC voltage setting. |  |  |  | 9D47 | 40263
39 |  | VMax |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Max Setting | AC voltage maximum setting used to adjust AC voltage maximum rating. |  |  |  | 9D48 | 40264
40 |  | VMin |  |  | uint16 |  | V_SF | V | RW |  |  | AC Voltage Min Setting | AC voltage minimum setting used to adjust AC voltage minimum rating. |  |  |  | 9D49 | 40265
41 |  | AMax |  |  | uint16 |  | A_SF | A | RW |  |  | AC Current Max Setting | Maximum AC current setting used to adjust maximum AC current rating. |  |  |  | 9D4A | 40266
42 |  | PFOvrExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Over-Excited Setting | Power factor over-excited setting. |  |  |  | 9D4B | 40267
43 |  | PFUndExt |  |  | uint16 |  | PF_SF |  | RW |  |  | PF Under-Excited Setting | Power factor under-excited setting. |  |  |  | 9D4C | 40268
44 |  | IntIslandCat |  |  | bitfield16 |  |  |  | RW |  |  | Intentional Island Categories | Intentional island categories. |  |  |  | 9D4D | 40269
|  | UNCATEGORIZED | 0 | [8 empty] | Uncategorized
|  | INT_ISL_CAPABLE | 1 | [8 empty] | Intentional Island-Capable
|  | BLACK_START_CAPABLE | 2 | [8 empty] | Black Start-Capable
|  | ISOCH_CAPABLE | 3 | [8 empty] | Isochronous-Capable
Scale Factors
45 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor. |  |  |  | 9D4E | 40270
46 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor. |  |  |  | 9D4F | 40271
47 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor. |  |  |  | 9D50 | 40272
48 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor. |  |  |  | 9D51 | 40273
49 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor. |  |  |  | 9D52 | 40274
50 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor. |  |  |  | 9D53 | 40275
51 |  | S_SF |  |  | sunssf | [5 empty] | S | Susceptance Scale Factor | Susceptance scale factor. |  |  |  | 9D54 | 40276

## 703
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DEREnterService |  |  | group | [6 empty] | Enter Service | Enter service model.
0 |  | ID | 703 |  | uint16 |  |  |  |  | M | S | Model ID | Enter service model ID. |  |  |  | 9D55 | 40277
1 |  | L | 17 |  | uint16 |  |  |  |  | M | S | Model Length | Enter service model length. |  |  |  | 9D56 | 40278
2 |  | ES |  |  | enum16 |  |  |  | RW |  |  | Permit Enter Service | Permit enter service. |  |  |  | 9D57 | 40279
|  | DISABLED | 0
|  | ENABLED | 1
3 |  | ESVHi |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage High | Enter service voltage high threshold as percent of normal voltage. |  |  |  | 9D58 | 40280
4 |  | ESVLo |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage Low | Enter service voltage low threshold as percent of normal voltage. |  |  |  | 9D59 | 40281
5 |  | ESHzHi |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency High | Enter service frequency high threshold. |  |  |  | 9D5A | 40282
7 |  | ESHzLo |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency Low | Enter service frequency low threshold. |  |  |  | 9D5C | 40284
9 |  | ESDlyTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Delay Time | Enter service delay time in seconds. |  |  |  | 9D5E | 40286
11 |  | ESRndTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Random Delay | Enter service random delay in seconds. |  |  |  | 9D60 | 40288
13 |  | ESRmpTms |  |  | uint32 |  |  | Secs | RW |  |  | Enter Service Ramp Time | Enter service ramp time in seconds. |  |  |  | 9D62 | 40290
15 |  | ESDlyRemTms |  |  | uint32 |  |  | Secs |  |  |  | Enter Service Delay Remaining | Enter service delay time remaining in seconds. |  |  |  | 9D64 | 40292
17 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage percentage scale factor. |  |  |  | 9D66 | 40294
18 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor. |  |  |  | 9D67 | 40295

## 704
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERCtlAC |  |  | group | [6 empty] | DER AC Controls | DER AC controls model.
0 |  | ID | 704 |  | uint16 |  |  |  |  | M | S | Model ID | DER AC controls model ID. |  |  |  | 9D68 | 40296
1 |  | L | 65 |  | uint16 |  |  |  |  | M | S | Model Length | DER AC controls model length. |  |  |  | 9D69 | 40297
Set Power Factor (when injecting active power)
2 |  | PFWInjEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Inj) Enable | Power factor enable when injecting active power. |  |  |  | 9D6A | 40298
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | PFWInjEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Inj) | Power factor reversion timer when injecting active power enable. |  |  |  | 9D6B | 40299
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
4 |  | PFWInjRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Inj) | Power factor reversion timer when injecting active power. |  |  |  | 9D6C | 40300
6 |  | PFWInjRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Inj) | Power factor reversion time remaining when injecting active power. |  |  |  | 9D6E | 40302
Set Power Factor (when absorbing active power)
8 |  | PFWAbsEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Abs) Enable | Power factor enable when absorbing active power. |  |  |  | 9D70 | 40304
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
9 |  | PFWAbsEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Power Factor Reversion Enable (W Abs) | Power factor reversion timer when absorbing active power enable. |  |  |  | 9D71 | 40305
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
10 |  | PFWAbsRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Abs) | Power factor reversion timer when absorbing active power. |  |  |  | 9D72 | 40306
12 |  | PFWAbsRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Abs) | Power factor reversion time remaining when absorbing active power. |  |  |  | 9D74 | 40308
Limit Maximum Active Power Generation
14 |  | WMaxLimPctEna |  |  | enum16 |  |  |  | RW |  |  | Limit Max Power Pct Enable | Limit maximum active power percent enable. |  |  |  | 9D76 | 40310
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
15 |  | WMaxLimPct |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Limit Max Power Pct Setpoint | Limit maximum active power percent value. |  |  |  | 9D77 | 40311
16 |  | WMaxLimPctRvrt |  |  | uint16 |  | WMaxLimPct_SF | Pct | RW |  |  | Reversion Limit Max Power Pct | Reversion limit maximum active power percent value. |  |  |  | 9D78 | 40312
17 |  | WMaxLimPctEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Limit Max Power Pct Enable | Reversion limit maximum active power percent value enable. |  |  |  | 9D79 | 40313
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
18 |  | WMaxLimPctRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Limit Max Power Pct Reversion Time | Limit maximum active power percent reversion time. |  |  |  | 9D7A | 40314
20 |  | WMaxLimPctRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Limit Max Power Pct Rev Time Rem | Limit maximum active power percent reversion time remaining. |  |  |  | 9D7C | 40316
Set Active Power Level (may be negative for charging)
22 |  | WSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Enable | Set active power enable. |  |  |  | 9D7E | 40318
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
23 |  | WSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Mode | Set active power mode. |  |  |  | 9D7F | 40319
|  | W_MAX_PCT | 0 | [8 empty] | Active Power As Max Percent | Active power setting is percentage of maximum active power.
|  | WATTS | 1 | [8 empty] | Active Power As Watts | Active power setting is in watts.
24 |  | WSet |  |  | int32 |  | WSet_SF | W | RW |  |  | Active Power Setpoint (W) | Active power setting value in watts. |  |  |  | 9D80 | 40320
26 |  | WSetRvrt |  |  | int32 |  | WSet_SF | W | RW |  |  | Reversion Active Power (W) | Reversion active power setting value in watts. |  |  |  | 9D82 | 40322
28 |  | WSetPct |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Active Power Setpoint (Pct) | Active power setting value as percent. |  |  |  | 9D84 | 40324
29 |  | WSetPctRvrt |  |  | int16 |  | WSetPct_SF | Pct | RW |  |  | Reversion Active Power (Pct) | Reversion active power setting value as percent. |  |  |  | 9D85 | 40325
30 |  | WSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Active Power Enable | Reversion active power function enable. |  |  |  | 9D86 | 40326
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
31 |  | WSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Active Power Reversion Time | Set active power reversion time. |  |  |  | 9D87 | 40327
33 |  | WSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Active Power Rev Time Rem | Set active power reversion time remaining. |  |  |  | 9D89 | 40329
Set Reacitve Power Level
35 |  | VarSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Enable | Set reactive power enable. |  |  |  | 9D8B | 40331
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
36 |  | VarSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Mode | Set reactive power mode. |  |  |  | 9D8C | 40332
|  | W_MAX_PCT | 0 | [8 empty] | Reactive Power As Watt Max Pct | Reactive power setting is percent of maximum active power.
|  | VAR_MAX_PCT | 1 | [8 empty] | Reactive Power As Var Max Pct | Reactive power setting is percent of maximum reactive power.
|  | VAR_AVAIL_PCT | 2 | [8 empty] | Reactive Power As Var Avail Pct | Reactive power setting is percent of available reactive power.
|  | VA_MAX_PCT | 3 | [8 empty] | Reactive Power As VA Max Pct | Reactive power setting is percent of maximum apparent power.
|  | VARS | 4 | [8 empty] | Reactive Power As Vars | Reactive power is in vars.
37 |  | VarSetPri |  |  | enum16 |  |  |  | RW |  |  | Reactive Power Priority | Reactive power priority. |  |  |  | 9D8D | 40333
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | VENDOR | 2 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
38 |  | VarSet |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reactive Power Setpoint (Vars) | Reactive power setting value in vars. |  |  |  | 9D8E | 40334
40 |  | VarSetRvrt |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reversion Reactive Power (Vars) | Reversion reactive power setting value in vars. |  |  |  | 9D90 | 40336
42 |  | VarSetPct |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reactive Power Setpoint (Pct) | Reactive power setting value as percent. |  |  |  | 9D92 | 40338
43 |  | VarSetPctRvrt |  |  | int16 |  | VarSetPct_SF | Pct | RW |  |  | Reversion Reactive Power (Pct) | Reversion reactive power setting value as percent. |  |  |  | 9D93 | 40339
44 |  | VarSetEnaRvrt |  |  | enum16 |  |  |  | RW |  |  | Reversion Reactive Power Enable | Reversion reactive power function enable. |  |  |  | 9D94 | 40340
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
45 |  | VarSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reactive Power Reversion Time | Set reactive power reversion time. |  |  |  | 9D95 | 40341
47 |  | VarSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reactive Power Rev Time Rem | Set reactive power reversion time remaining. |  |  |  | 9D97 | 40343
Ramp Rate
49 |  | WRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Normal Ramp Rate | Ramp rate for increases in active power during normal generation. |  |  |  | 9D99 | 40345
50 |  | WRmpRef |  |  | enum16 |  |  |  | RW |  |  | Normal Ramp Rate Reference | Ramp rate reference unit for increases in active power or current during normal generation. |  |  |  | 9D9A | 40346
|  | A_MAX | 0 | [8 empty] | Max Current Ramp | Ramp based on percent of max current per second.
|  | W_MAX | 1 | [8 empty] | Max Active Power Ramp | Ramp based on percent of max active power per second.
51 |  | VarRmp |  |  | uint16 |  |  | %Max/Sec | RW |  |  | Reactive Power Ramp Rate | Ramp rate based on max reactive power per second. |  |  |  | 9D9B | 40347
52 |  | AntiIslEna |  |  | enum16 |  |  |  | RW |  |  | Anti-Islanding Enable | Anti-islanding enable. |  |  |  | 9D9C | 40348
|  | DISABLED | 0 | [8 empty] | Disabled | Anti-islanding is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Anti-islanding is enabled.
Scale Factors
53 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor. |  |  |  | 9D9D | 40349
54 |  | WMaxLimPct_SF |  |  | sunssf | [5 empty] | S | Limit Max Power Scale Factor | Limit maximum power scale factor. |  |  |  | 9D9E | 40350
55 |  | WSet_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor. |  |  |  | 9D9F | 40351
56 |  | WSetPct_SF |  |  | sunssf | [5 empty] | S | Active Power Pct Scale Factor | Active power pct scale factor. |  |  |  | 9DA0 | 40352
57 |  | VarSet_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor. |  |  |  | 9DA1 | 40353
58 |  | VarSetPct_SF |  |  | sunssf | [5 empty] | S | Reactive Power Pct Scale Factor | Reactive power pct scale factor. |  |  |  | 9DA2 | 40354
Power Factor Settings
|  | DERCtlAC.PFWInj |  |  | sync | [6 empty] | Power Factor (W Inj) | Power factor setpoint when injecting active power.
59 | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Inj) | Power factor setpoint when injecting active power. |  |  |  | 9DA3 | 40355
60 | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Inj) | Power factor excitation setpoint when injecting active power. |  |  |  | 9DA4 | 40356
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWInjRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
61 | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power. |  |  |  | 9DA5 | 40357
62 | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Inj) | Reversion power factor excitation setpoint when injecting active power. |  |  |  | 9DA6 | 40358
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbs |  |  | sync | [6 empty] | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
63 | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Abs) | Power factor setpoint when absorbing active power. |  |  |  | 9DA7 | 40359
64 | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Abs) | Power factor excitation setpoint when absorbing active power. |  |  |  | 9DA8 | 40360
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbsRvrt |  |  | sync | [6 empty] | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
65 | 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power. |  |  |  | 9DA9 | 40361
66 | 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Abs) | Reversion power factor excitation setpoint when absorbing active power. |  |  |  | 9DAA | 40362
|  | OVER_EXCITED | 0 | [8 empty] | Over-Excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-Excited | Power factor under-excited excitation.

## 705
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERVoltVar |  |  | group | [6 empty] | DER Volt-Var | DER Volt-Var model.
0 |  | ID | 705 |  | uint16 |  |  |  |  | M | S | Model ID | DER Volt-Var model ID. |  |  |  | 9DAB | 40363
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Volt-Var model length. |  |  |  | 9DAC | 40364
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Volt-Var Module Enable | Volt-Var control enable. |  |  | Read only | 9DAD | 40365
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  |  | Read only | 9DAE | 40366
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  |  |  | 9DAF | 40367
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  |  |  | 9DB0 | 40368
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  |  |  | 9DB1 | 40369
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time. |  |  |  | 9DB2 | 40370
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Remaining | Reversion time remaining in seconds. |  |  |  | 9DB4 | 40372
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout. |  |  |  | 9DB6 | 40374
12 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  |  |  | 9DB7 | 40375
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Var Scale Factor | Scale factor for curve var points. |  |  |  | 9DB8 | 40376
14 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor. |  |  |  | 9DB9 | 40377
Stored Curve Sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERVoltVar.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points. |  |  | Read only |  | 40378+(50*CrvIdx)
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference. |  |  | Read only |  | 40379+(50*CrvIdx)
|  | W_MAX_PCT | 0 | [8 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 1 | [8 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 2 | [8 empty] | Percent Available Vars
|  | VA_MAX_PCT | 3 | [8 empty] | Percent Max Apparent Power
| 2 | Pri |  |  | enum16 |  |  |  | RW |  |  | Power Priority | Power priority. |  |  |  |  | 40380+(50*CrvIdx)
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | VENDOR | 2 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
| 3 | VRef |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Vref Adjustment | Vref adjustment as percentage of nominal voltage. |  |  |  |  | 40381+(50*CrvIdx)
| 4 | VRefAuto |  |  | uint16 |  | V_SF | VRefPct |  |  |  | Current Autonomous Vref | Autonomous vref value as a percentage of nominal voltage. |  |  |  |  | 40382+(50*CrvIdx)
| 5 | VRefAutoEna |  |  | enum16 |  |  |  | RW |  |  | Autonomous Vref Enable | Enable autonomous vref. |  |  |  |  | 40383+(50*CrvIdx)
|  | DISABLED | 0 | [8 empty] | Disabled Flag | Disabled flag (Disabled = 0, Enabled = 1).
|  | ENABLED | 1 | [8 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
| 6 | VRefAutoTms |  |  | uint16 |  |  | Secs | RW |  |  | Auto Vref Time Constant | Autonomous vref time constant. |  |  |  |  | 40384+(50*CrvIdx)
| 7 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW |  |  | Open Loop Response Time | Open loop response time. |  |  | Read only |  | 40385+(50*CrvIdx)
| 9 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  |  |  |  | 40387+(50*CrvIdx)
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored Curve Sets - Curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltVar.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points. |  |  | Read only
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage. |  |  | Read only |  | 40388+(50*CrvIdx)+(2*PtIdx)
| 1 | Var |  |  | int16 |  | DeptRef_SF | DeptRef | RW |  |  | Reactive Power Point | Curve reactive power point as set in DeptRef point. |  |  | Read only |  | 40389+(50*CrvIdx)+(2*PtIdx)

## 706
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERVoltWatt |  |  | group | [6 empty] | DER Volt-Watt | DER Volt-Watt model.
0 |  | ID | 706 |  | uint16 |  |  |  |  | M | S | Model ID | DER Volt-Watt model ID. |  |  |  | 9EB4 | 40628
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Volt-Watt model length. |  |  |  | 9EB5 | 40629
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Volt-Watt Module Enable | Volt-Watt control enable. |  |  | Read only | 9EB6 | 40630
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1. |  |  | Read only | 9EB7 | 40631
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation. |  |  |  | 9EB8 | 40632
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported. |  |  |  | 9EB9 | 40633
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported. |  |  |  | 9EBA | 40634
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time. |  |  |  | 9EBB | 40635
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Remaining | Reversion time remaining in seconds. |  |  |  | 9EBD | 40637
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout. |  |  |  | 9EBF | 40639
12 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points. |  |  |  | 9EC0 | 40640
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Watt Scale Factor | Scale factor for curve watt points. |  |  |  | 9EC1 | 40641
14 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor. |  |  |  | 9EC2 | 40642
Stored curve sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERVoltWatt.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points. |  |  | Read only |  | 40643+(45*CrvIdx)
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference. |  |  | Read only |  | 40644+(45*CrvIdx)
|  | W_MAX_PCT | 0
|  | W_AVAL_PCT | 1
| 2 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW |  |  | Open Loop Response Time | Open loop response time. |  |  | Read only |  | 40645+(45*CrvIdx)
| 4 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access. |  |  |  |  | 40647+(45*CrvIdx)
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltWatt.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points. |  |  | Read only
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage. |  |  | Read only |  | 40648+(45*CrvIdx)+(2*PtIdx)
| 1 | W |  |  | int16 |  | DeptRef_SF | DeptRef | RW |  |  | Dependent Reference | Active power in percent of rated active power. |  |  | Read only |  | 40649+(45*CrvIdx)+(2*PtIdx)

## 713
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERStorageCapacity |  |  | group | [6 empty] | DER Storage Capacity | DER storage capacity.
0 |  | ID | 713 |  | uint16 |  |  |  |  | M | S | Model ID | DER storage capacity model ID. |  |  |  | 9FA4 | 40868
1 |  | L | 7 |  | uint16 |  |  |  |  | M | S | Model Length | DER storage capacity model length. |  |  |  | 9FA5 | 40869
2 |  | WHRtg |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Rating | Energy rating of the DER storage. |  |  |  | 9FA6 | 40870
3 |  | WHAvail |  |  | uint16 |  | WH_SF | WH |  |  |  | Energy Available | Energy available of the DER storage (WHAvail = WHRtg * SoC * SoH) |  |  |  | 9FA7 | 40871
4 |  | SoC |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Charge | State of charge of the DER storage. |  |  |  | 9FA8 | 40872
5 |  | SoH |  |  | uint16 |  | Pct_SF | Pct |  |  |  | State of Health | State of health of the DER storage. |  |  |  | 9FA9 | 40873
6 |  | Sta |  |  | enum16 | [6 empty] | Status | Storage status. |  |  |  | 9FAA | 40874
|  | OK | 0 | [8 empty] | OK | No warnings or errors pending.
|  | WARNING | 1 | [8 empty] | Warning | One or more warnings pending.
|  | ERROR | 2 | [8 empty] | Error | One or more errors pending.
7 |  | WH_SF |  |  | sunssf | [5 empty] | S | Energy Scale Factor | Scale factor for energy capacity. |  |  |  | 9FAB | 40875
8 |  | Pct_SF |  |  | sunssf | [5 empty] | S | Percent Scale Factor | Scale factor for percentage. |  |  |  | 9FAC | 40876

## 715
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | DERCtl |  |  | group | [6 empty] | DERCtl | DER Control
0 |  | ID | 715 |  | uint16 |  |  |  |  | M |  | Model ID | DER control model ID. |  |  |  | 9FAD | 40877
1 |  | L | 7 |  | uint16 |  |  |  |  | M |  | Model Length | DER control model length. |  |  |  | 9FAE | 40878
DER Controls
2 |  | LocRemCtl |  |  | enum16 | [6 empty] | Control Mode | DER control mode. Enumeration. |  |  |  | 9FAF | 40879
|  | REMOTE | 0 | [8 empty] | Remote Control
|  | LOCAL | 1 | [8 empty] | Local Control | Local mode is required for manual/maintenance operations. Once invoked, it must be explicitly exited for the inverter to be controlled remotely.
3 |  | DERHb |  |  | uint32 | [6 empty] | DER Heartbeat | Value is incremented every second by the DER with periodic resets to zero. |  |  |  | 9FB0 | 40880
5 |  | ControllerHb |  |  | uint32 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second by the controller with periodic resets to zero. |  |  |  | 9FB2 | 40882
7 |  | AlarmReset |  |  | uint16 |  |  |  | RW |  |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset. |  |  |  | 9FB4 | 40884
8 |  | OpCtl |  |  | enum16 |  |  |  | RW |  |  | Set Operation | Commands to PCS. Enumerated value. |  |  |  | 9FB5 | 40885
|  | STOP | 0 | [8 empty] | Stop the DER
|  | START | 1 | [8 empty] | Start the DER
|  | ENTER_STANDBY | 2 | [8 empty] | Enter Standby Mode
|  | EXIT_STANDBY | 3 | [8 empty] | Exit Standby Mode

## 801 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | storage |  |  | group | [6 empty] | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
0 |  | ID | 801 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | DEPRECATED |  |  | enum16 |  |  |  |  | M |  | Deprecated Model | This model has been deprecated.

## 802
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | battery |  |  | group | [6 empty] | Battery Base Model
0 |  | ID | 802 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  |  |  | 9FB6 | 40886
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  |  |  | 9FB7 | 40887
2 |  | AHRtg |  |  | uint16 |  | AHRtg_SF | Ah |  | M |  | Nameplate Charge Capacity | Nameplate charge capacity in amp-hours. |  |  |  | 9FB8 | 40888
3 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  | M |  | Nameplate Energy Capacity | Nameplate energy capacity in DC watt-hours. |  |  |  | 9FB9 | 40889
4 |  | WChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Charge Rate | Maximum rate of energy transfer into the storage device in DC watts. |  |  |  | 9FBA | 40890
5 |  | WDisChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Discharge Rate | Maximum rate of energy transfer out of the storage device in DC watts. |  |  |  | 9FBB | 40891
6 |  | DisChaRte |  |  | uint16 |  | DisChaRte_SF | %WHRtg |  |  |  | Self Discharge Rate | Self discharge rate. Percentage of capacity (WHRtg) discharged per day. |  |  |  | 9FBC | 40892
7 |  | SoCMax |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Max SoC | Manufacturer maximum state of charge, expressed as a percentage. |  |  |  | 9FBD | 40893
8 |  | SoCMin |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Min SoC | Manufacturer minimum state of charge, expressed as a percentage. |  |  |  | 9FBE | 40894
9 |  | SocRsvMax |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Max Reserve Percent | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage. |  |  |  | 9FBF | 40895
10 |  | SoCRsvMin |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Min Reserve Percent | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage. |  |  |  | 9FC0 | 40896
11 |  | SoC |  |  | uint16 |  | SoC_SF | %WHRtg |  | M |  | State of Charge | State of charge, expressed as a percentage. |  |  |  | 9FC1 | 40897
12 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge, expressed as a percentage. |  |  |  | 9FC2 | 40898
13 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | State of Health | Percentage of battery life remaining. |  |  |  | 9FC3 | 40899
14 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Number of cycles executed in the battery. |  |  |  | 9FC4 | 40900
16 |  | ChaSt |  |  | enum16 | [6 empty] | Charge Status | Charge status of storage device. Enumeration. |  |  |  | 9FC6 | 40902
|  | OFF | 1
|  | EMPTY | 2
|  | DISCHARGING | 3
|  | CHARGING | 4
|  | FULL | 5
|  | HOLDING | 6
|  | TESTING | 7
17 |  | LocRemCtl |  |  | enum16 |  |  |  |  | M |  | Control Mode | Battery control mode. Enumeration. |  |  |  | 9FC7 | 40903
|  | REMOTE | 0
|  | LOCAL | 1
18 |  | Hb |  |  | uint16 | [6 empty] | Battery Heartbeat | Value is incremented every second with periodic resets to zero. |  |  |  | 9FC8 | 40904
19 |  | CtrlHb |  |  | uint16 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second with periodic resets to zero. |  |  |  | 9FC9 | 40905
20 |  | AlmRst |  |  | uint16 |  |  |  | RW | M |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset. |  |  |  | 9FCA | 40906
21 |  | Typ |  |  | enum16 |  |  |  |  | M |  | Battery Type | Type of battery. Enumeration. |  |  |  | 9FCB | 40907
|  | NOT APPLICABLE_UNKNOWN | 0
|  | LEAD_ACID | 1
|  | NICKEL_METAL_HYDRATE | 2
|  | NICKEL_CADMIUM | 3
|  | LITHIUM_ION | 4
|  | CARBON_ZINC | 5
|  | ZINC_CHLORIDE | 6
|  | ALKALINE | 7
|  | RECHARGEABLE_ALKALINE | 8
|  | SODIUM_SULFUR | 9
|  | FLOW | 10
|  | OTHER | 99
22 |  | State |  |  | enum16 |  |  |  |  | M |  | State of the Battery Bank | State of the battery bank. Enumeration. |  |  |  | 9FCC | 40908
|  | DISCONNECTED | 1
|  | INITIALIZING | 2
|  | CONNECTED | 3
|  | STANDBY | 4
|  | SOC PROTECTION | 5
|  | SUSPENDING | 6
|  | FAULT | 99
23 |  | StateVnd |  |  | enum16 | [6 empty] | Vendor Battery Bank State | Vendor specific battery bank state. Enumeration. |  |  |  | 9FCD | 40909
24 |  | WarrDt |  |  | uint32 | [6 empty] | Warranty Date | Date the device warranty expires. |  |  |  | 9FCE | 40910
26 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 1 Bitfield | Alarms and warnings. Bit flags. |  |  |  | 9FD0 | 40912
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | CURRENT_IMBALANCE_WARNING | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_1 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
28 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 2 Bitfield | Alarms and warnings. Bit flags. |  |  |  | 9FD2 | 40914
30 |  | EvtVnd1 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 1 | Vendor defined events. |  |  |  | 9FD4 | 40916
32 |  | EvtVnd2 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 2 | Vendor defined events. |  |  |  | 9FD6 | 40918
34 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | External Battery Voltage | DC Bus Voltage. |  |  |  | 9FD8 | 40920
35 |  | VMax |  |  | uint16 |  | V_SF | V |  |  |  | Max Battery Voltage | Instantaneous maximum battery voltage. |  |  |  | 9FD9 | 40921
36 |  | VMin |  |  | uint16 |  | V_SF | V |  |  |  | Min Battery Voltage | Instantaneous minimum battery voltage. |  |  |  | 9FDA | 40922
37 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Max Cell Voltage | Maximum voltage for all cells in the bank. |  |  |  | 9FDB | 40923
38 |  | CellVMaxStr |  |  | uint16 | [6 empty] | Max Cell Voltage String | String containing the cell with maximum voltage. |  |  |  | 9FDC | 40924
39 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with maximum voltage. |  |  |  | 9FDD | 40925
40 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage | Minimum voltage for all cells in the bank. |  |  |  | 9FDE | 40926
41 |  | CellVMinStr |  |  | uint16 | [6 empty] | Min Cell Voltage String | String containing the cell with minimum voltage. |  |  |  | 9FDF | 40927
42 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with minimum voltage. |  |  |  | 9FE0 | 40928
43 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average cell voltage for all cells in the bank. |  |  |  | 9FE1 | 40929
44 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Total DC Current | Total DC current flowing to/from the battery bank. |  |  |  | 9FE2 | 40930
45 |  | AChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Charge Current | Instantaneous maximum DC charge current. |  |  |  | 9FE3 | 40931
46 |  | ADisChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Discharge Current | Instantaneous maximum DC discharge current. |  |  |  | 9FE4 | 40932
47 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Total Power | Total power flowing to/from the battery bank. |  |  |  | 9FE5 | 40933
48 |  | ReqInvState |  |  | enum16 | [6 empty] | Inverter State Request | Request from battery to start or stop the inverter. Enumeration. |  |  |  | 9FE6 | 40934
|  | NO REQUEST | 0
|  | START | 1
|  | STOP | 2
49 |  | ReqW |  |  | int16 |  | W_SF | W |  |  |  | Battery Power Request | AC Power requested by battery. |  |  |  | 9FE7 | 40935
50 |  | SetOp |  |  | enum16 |  |  |  | RW | M |  | Set Operation | Instruct the battery bank to perform an operation such as connecting. Enumeration. |  |  |  | 9FE8 | 40936
|  | CONNECT | 1
|  | DISCONNECT | 2
51 |  | SetInvState |  |  | enum16 |  |  |  | RW | M |  | Set Inverter State | Set the current state of the inverter. |  |  |  | 9FE9 | 40937
|  | INVERTER_STOPPED | 1
|  | INVERTER_STANDBY | 2
|  | INVERTER_STARTED | 3
52 |  | AHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for charge capacity. |  |  |  | 9FEA | 40938
53 |  | WHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for energy capacity. |  |  |  | 9FEB | 40939
54 |  | WChaDisChaMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for maximum charge and discharge rate. |  |  |  | 9FEC | 40940
55 |  | DisChaRte_SF |  |  | sunssf | [7 empty] | Scale factor for self discharge rate. |  |  |  | 9FED | 40941
56 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for state of charge values. |  |  |  | 9FEE | 40942
57 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for depth of discharge. |  |  |  | 9FEF | 40943
58 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for state of health. |  |  |  | 9FF0 | 40944
59 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC bus voltage. |  |  |  | 9FF1 | 40945
60 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage. |  |  |  | 9FF2 | 40946
61 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC current. |  |  |  | 9FF3 | 40947
62 |  | AMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for instantaneous DC charge/discharge current. |  |  |  | 9FF4 | 40948
63 |  | W_SF |  |  | sunssf | [7 empty] | Scale factor for AC power request. |  |  |  | 9FF5 | 40949

## 803
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | lithium_ion_bank |  |  | group | [6 empty] | Lithium-Ion Battery Bank Model
0 |  | ID | 803 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  |  |  | 9FF6 | 40950
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  |  |  | 9FF7 | 40951
2 |  | NStr |  |  | uint16 |  |  |  |  | M |  | String Count | Number of strings in the bank. |  |  |  | 9FF8 | 40952
3 |  | NStrCon |  |  | uint16 |  |  |  |  | M |  | Connected String Count | Number of strings with contactor closed. |  |  |  | 9FF9 | 40953
4 |  | ModTmpMax |  |  | int16 |  | ModTmp_SF |  |  | M |  | Max Module Temperature | Maximum temperature for all modules in the bank. |  |  |  | 9FFA | 40954
5 |  | ModTmpMaxStr |  |  | uint16 | [6 empty] | Max Module Temperature String | String containing the module with maximum temperature. |  |  |  | 9FFB | 40955
6 |  | ModTmpMaxMod |  |  | uint16 | [6 empty] | Max Module Temperature Module | Module with maximum temperature. |  |  |  | 9FFC | 40956
7 |  | ModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the bank. |  |  |  | 9FFD | 40957
8 |  | ModTmpMinStr |  |  | uint16 | [6 empty] | Min Module Temperature String | String containing the module with minimum temperature. |  |  |  | 9FFE | 40958
9 |  | ModTmpMinMod |  |  | uint16 | [6 empty] | Min Module Temperature Module | Module with minimum temperature. |  |  |  | 9FFF | 40959
10 |  | ModTmpAvg |  |  | int16 | [6 empty] | Average Module Temperature | Average temperature for all modules in the bank. |  |  |  | A000 | 40960
11 |  | StrVMax |  |  | uint16 |  | V_SF | V |  |  |  | Max String Voltage | Maximum string voltage for all strings in the bank. |  |  |  | A001 | 40961
12 |  | StrVMaxStr |  |  | uint16 | [6 empty] | Max String Voltage String | String with maximum voltage. |  |  |  | A002 | 40962
13 |  | StrVMin |  |  | uint16 |  | V_SF | V |  |  |  | Min String Voltage | Minimum string voltage for all strings in the bank. |  |  |  | A003 | 40963
14 |  | StrVMinStr |  |  | uint16 | [6 empty] | Min String Voltage String | String with minimum voltage. |  |  |  | A004 | 40964
15 |  | StrVAvg |  |  | uint16 |  | V_SF | V |  |  |  | Average String Voltage | Average string voltage for all strings in the bank. |  |  |  | A005 | 40965
16 |  | StrAMax |  |  | int16 |  | A_SF | A |  |  |  | Max String Current | Maximum current of any string in the bank. |  |  |  | A006 | 40966
17 |  | StrAMaxStr |  |  | uint16 | [6 empty] | Max String Current String | String with the maximum current. |  |  |  | A007 | 40967
18 |  | StrAMin |  |  | int16 |  | A_SF | A |  |  |  | Min String Current | Minimum current of any string in the bank. |  |  |  | A008 | 40968
19 |  | StrAMinStr |  |  | uint16 | [6 empty] | Min String Current String | String with the minimum current. |  |  |  | A009 | 40969
20 |  | StrAAvg |  |  | int16 |  | A_SF | A |  |  |  | Average String Current | Average string current for all strings in the bank. |  |  |  | A00A | 40970
21 |  | NCellBal |  |  | uint16 | [6 empty] | Battery Cell Balancing Count | Total number of cells that are currently being balanced. |  |  |  | A00B | 40971
22 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage. |  |  |  | A00C | 40972
23 |  | ModTmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperatures. |  |  |  | A00D | 40973
24 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string currents. |  |  |  | A00E | 40974
25 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for string state of health. |  |  |  | A00F | 40975
26 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string state of charge. |  |  |  | A010 | 40976
27 |  | V_SF |  |  | sunssf | [7 empty] | Scale factor for string voltage. |  |  |  | A011 | 40977
|  | lithium_ion_bank.string |  | 0 | group
| 0 | StrNMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Count of modules in the string. |  |  |  |  | 40978+(32*StringIdx)
| 1 | StrSt |  |  | bitfield32 |  |  |  |  | M |  | String Status | Current status of the string. |  |  |  |  | 40979+(32*StringIdx)
|  | STRING_ENABLED | 0
|  | CONTACTOR_STATUS | 1
| 3 | StrConFail |  |  | enum16 | [6 empty] | Connection Failure Reason | [5 empty] | 40981+(32*StringIdx)
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | STR_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | STRING_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | STRING_FAULT | 8
| 4 | StrSoC |  |  | uint16 |  | SoC_SF | % |  | M |  | String State of Charge | Battery string state of charge, expressed as a percentage. |  |  |  |  | 40982+(32*StringIdx)
| 5 | StrSoH |  |  | uint16 |  | SoH_SF | % |  |  |  | String State of Health | Battery string state of health, expressed as a percentage. |  |  |  |  | 40983+(32*StringIdx)
| 6 | StrA |  |  | int16 |  | A_SF | A |  | M |  | String Current | String current measurement. |  |  |  |  | 40984+(32*StringIdx)
| 7 | StrCellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the string. |  |  |  |  | 40985+(32*StringIdx)
| 8 | StrCellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the maximum cell voltage. |  |  |  |  | 40986+(32*StringIdx)
| 9 | StrCellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the string. |  |  |  |  | 40987+(32*StringIdx)
| 10 | StrCellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the minimum cell voltage. |  |  |  |  | 40988+(32*StringIdx)
| 11 | StrCellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the string. |  |  |  |  | 40989+(32*StringIdx)
| 12 | StrModTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Module Temperature | Maximum temperature for all modules in the bank. |  |  |  |  | 40990+(32*StringIdx)
| 13 | StrModTmpMaxMod |  |  | uint16 | [6 empty] | Max Module Temperature Module | Module with the maximum temperature. |  |  |  |  | 40991+(32*StringIdx)
| 14 | StrModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the bank. |  |  |  |  | 40992+(32*StringIdx)
| 15 | StrModTmpMinMod |  |  | uint16 | [6 empty] | Min Module Temperature Module | Module with the minimum temperature. |  |  |  |  | 40993+(32*StringIdx)
| 16 | StrModTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Module Temperature | Average temperature for all modules in the bank. |  |  |  |  | 40994+(32*StringIdx)
| 17 | StrDisRsn |  |  | enum16 | [6 empty] | Disabled Reason | Reason why the string is currently disabled. |  |  |  |  | 40995+(32*StringIdx)
|  | NONE | 0
|  | FAULT | 1
|  | MAINTENANCE | 2
|  | EXTERNAL | 3
|  | OTHER | 4
| 18 | StrConSt |  |  | bitfield32 | [6 empty] | Contactor Status | Status of the contactor(s) for the string. |  |  |  |  | 40996+(32*StringIdx)
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
| 20 | StrEvt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags. |  |  |  |  | 40998+(32*StringIdx)
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_1 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_2 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
| 22 | StrEvt2 |  |  | bitfield32 | [6 empty] | String Event 2 | Alarms, warnings and status values. Bit flags. |  |  |  |  | 41000+(32*StringIdx)
| 24 | StrEvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor String Event Bitfield 1 | Vendor defined events. |  |  |  |  | 41002+(32*StringIdx)
| 26 | StrEvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor String Event Bitfield 2 | Vendor defined events. |  |  |  |  | 41004+(32*StringIdx)
| 28 | StrSetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable String | Enables and disables the string. |  |  |  |  | 41006+(32*StringIdx)
|  | ENABLE_STRING | 1
|  | DISABLE_STRING | 2
| 29 | StrSetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect String | Connects and disconnects the string. |  |  |  |  | 41007+(32*StringIdx)
|  | CONNECT_STRING | 1
|  | DISCONNECT_STRING | 2
| 30 | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register. |  |  |  |  | 41008+(32*StringIdx)
| 31 | Pad2 |  |  | pad |  |  |  |  | M |  | Pad | Pad register. |  |  |  |  | 41009+(32*StringIdx)

## 64901
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | socomec_pms |  |  | group | [6 empty] | Socomec PMS | Vendor model providing PMS states, warnings and alarms details
0 |  | ID | 64901 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  |  |  | A312 | 41746
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  |  |  | A313 | 41747
States Word 1
2 |  | SW1 |  |  | bitfield16 | [6 empty] | States Word 1 | States Word 1 |  |  |  | A314 | 41748
|  | S000 - Battery-On Command | 0 | [8 empty] | Battery connection order. | The battery is ordered to connect to the inverter.(DC side)
|  | S001 - Inverter On Command | 1 | [8 empty] | Inverter connection order. | The inverter is ordered to connect to the grid.(AC side)
|  | S002 - N/A | 2
|  | S003 - N/A | 3
|  | S004 - Battery Ready | 4 | [8 empty] | Battery connection status. | The battery is ready and connected to the inverter.(DC side)
|  | S005 - Inverter Ready | 5 | [8 empty] | Inverter connection status. | The inverter is ready and connected to the grid if allowed.(AC side)
|  | S006 - Sleep Active | 6 | [8 empty] | Sleep mode is active. | The ESS is in sleep mode.
|  | S007 - Alarm State | 7 | [8 empty] | ESS is in alarm | The ESS is in alarm.
|  | S008 - Idle Mode | 8 | [8 empty] | Idle mode is active. | The ESS is in idle mode. The power setpoints are 0 and they will resume normally after leaving this mode.
|  | S009 - Charging | 9 | [8 empty] | ESS is charging | The ESS is charging the battery. P is negative.
|  | S010 - Discharging | 10 | [8 empty] | ESS is discharging | The ESS is discharging the battery. P is positive.
|  | S011 - General Critical Alarm | 11 | [9 empty] | (Legacy)
|  | S012 - General Alarm | 12 | [8 empty] | ESS is in alarm. | At least one alarm is present on the ESS.
|  | S013 - General Warning | 13 | [8 empty] | ESS is in warning. | At least one warning is present on the ESS.
|  | S014 - Battery Can Be Charged | 14 | [8 empty] | Battery can be charged. | The ESS will charge the battery if active power setpoint is negative.
|  | S015 - Battery Can Be Discharged | 15 | [8 empty] | Battery can be discharged. | The ESS will discharge the battery if active power setpoint is positive.
States Word 2
3 |  | SW2 |  |  | bitfield16 | [6 empty] | States Word 2 | States Word 2 |  |  |  | A315 | 41749
|  | S016 - N/A | 0
|  | S017 - On Grid Mode | 1 | [8 empty] | ESS in On-Grid Mode. | The ESS is connected and in On-Grid Mode. Power setpoints can be sent.
|  | S018 - Off Grid Mode | 2 | [8 empty] | ESS in Off-Grid Mode. | Applicable for Off-Grid Operations. The ESS is connected and in Off-Grid Mode. The ESS is forming its own grid and autonomously regulates it.
|  | S019 - Force Islanding Command | 3 | [8 empty] | Islanding is requested. | Applicable for Off-Grid Operations. The ESS will try to move and stay in Off-Grid Mode even if the main grid is present.
|  | S020 - Un-Programmed Islanding Enabled Command | 4 | [8 empty] | Un-Programmed Islanding is enabled. | Applicable for Off-Grid Operations. The ESS will try to move into Off-Grid Mode if the main grid is lost.
|  | S021 - Black Start Enabled Command | 5 | [8 empty] | Black Start is enabled. | Applicable for Off-Grid Operations. The ESS will try to move into Off-Grid Mode through the blackstart process if the main grid is lost.
|  | S022 - Black Start Ended | 6 | [8 empty] | Black Start has ended. | Applicable for Off-Grid Operations. The black start procedure has just ended.
|  | S023 - N/A | 7
|  | S024 - Zero-Power In Progress | 8 | [8 empty] | Power ramp for planned islanding is in progress. | Applicable for Off-Grid Operations. The ESS is performing a zero-power ramp at the point of interconnection during the planned islanding sequence.
|  | S025 - Programmed Islanding | 9 | [8 empty] | Planned islanding is in progress. | Applicable for Off-Grid Operations. The ESS is performing the planned(or programmed) islanding sequence.
|  | S026 - Un-Programmed Islanding | 10 | [8 empty] | Unplanned islanding is in progress. | Applicable for Off-Grid Operations. The ESS is performing the planned(or un-programmed) islanding sequence.
|  | S027 - Black Start In Progress | 11 | [8 empty] | Black Start is in progress. | Applicable for Off-Grid Operations. The ESS is performing the black start sequence.
|  | S028 - Synchronization In Progress | 12 | [8 empty] | Synchronization is in progress. | Applicable for Off-Grid Operations. The ESS is performing the synchronization sequence to seamlessly get back to the main grid.
|  | S029 - P(f) In Progress | 13 | [9 empty] | (Legacy) Applicable for Off-Grid Operations.
|  | S030 - PCS drying in progress | 14 | [8 empty] | Converter drying is in progress. | The converter is performing a drying sequence due to a prolonged stop of the auxiliaries.
|  | S031 - Local Mode Active | 15 | [8 empty] | ESS is in local mode. | The ESS is in local mode and can only be operated through the HMI.
States Word 3
4 |  | SW3 |  |  | bitfield16 | [6 empty] | States Word 3 | States Word 3 |  |  |  | A316 | 41750
|  | S032 - Remote Mode Active | 0 | [8 empty] | ESS is in remote mode. | The ESS is in remote mode and can be operated through the Sunspec interface.
|  | S033 - Grid Voltage Ok | 1 | [8 empty] | Main grid is present. | The main grid voltage is inside defined range and therefore present.
|  | S034 - Micro Grid Voltage Ok | 2 | [8 empty] | Micro grid is present. | The micro grid voltage is inside defined range and therefore present.
|  | S035 - Micro Grid Voltage Null | 3 | [8 empty] | Micro grid is absent. | The micro grid voltage is out of defined range and therefore absent.
|  | S036 - N/A | 4
|  | S037 - N/A | 5
|  | S038 - N/A | 6
|  | S039 - N/A | 7
|  | S040 - N/A | 8
|  | S041 - N/A | 9
|  | S042 - N/A | 10
|  | S043 - N/A | 11
|  | S044 - N/A | 12
|  | S045 - N/A | 13
|  | S046 - N/A | 14
|  | S047 - N/A | 15
States Word 4
5 |  | SW4 |  |  | bitfield16 | [6 empty] | States Word 4 | States Word 4 |  |  |  | A317 | 41751
|  | S048 - IC Configuration completed | 0 | [8 empty] | Islanding Controller configured. | Applicable for Off-Grid Operations. The islanding controller has received a set of configuration.
|  | S049 - IC Syncronization in progress | 1 | [8 empty] | Islanding Controller synch is in progress. | Applicable for Off-Grid Operations. The islanding controller synchronization to seamlessly get back to the main grid is in progress.
|  | S050 - IC Coupling Status | 2 | [8 empty] | Islanding Controller Coupling is ok. | Applicable for Off-Grid Operations. The main grid and the micro grid are synchronized.
|  | S051 - IC Grid Voltage inside thr | 3 | [8 empty] | Islanding Controller Main grid is present. | Applicable for Off-Grid Operations. The main grid voltage measured by the islanding controller is inside defined range and therefore present.
|  | S052 - IC Grid voltage null | 4 | [8 empty] | Islanding Controller Main grid is absent. | Applicable for Off-Grid Operations. The main grid voltage measured by the islanding controller is out of defined range and therefore absent.
|  | S053 - IC uGrid Voltage inside thr | 5 | [8 empty] | Islanding Controller Micro grid is present. | Applicable for Off-Grid Operations. The micro grid voltage measured by the islanding controller is inside defined range and therefore present.
|  | S054 - IC uGrid voltage null | 6 | [8 empty] | Islanding Controller Migro grid is absent. | Applicable for Off-Grid Operations. The micro grid voltage measured by the islanding controller is out of defined range and therefore absent.
|  | S055 - IC Voltage difference inside thr | 7 | [8 empty] | Islanding Controller voltages difference ok. | Applicable for Off-Grid Operations. The difference between micro grid and main grid voltages measured by the islanding controller is inside defined range and therefore ok.
|  | S056 - IC Frequency differenze inside thr | 8 | [8 empty] | Islanding Controller frequencies difference ok. | Applicable for Off-Grid Operations. The difference between micro grid and main grid frequencies measured by the islanding controller is inside defined range and therefore ok.
|  | S057 - IC Phase difference inside thr | 9 | [8 empty] | Islanding Controller phases difference ok. | Applicable for Off-Grid Operations. The difference between micro grid and main grid phases measured by the islanding controller is inside defined range and therefore ok.
|  | S058 - N/A | 10
|  | S059 - N/A | 11
|  | S060 - N/A | 12
|  | S061 - N/A | 13
|  | S062 - N/A | 14
|  | S063 - N/A | 15
States Word 5
6 |  | SW5 |  |  | bitfield16 | [6 empty] | States Word 5 | States Word 5 |  |  |  | A318 | 41752
|  | S064 - Battery Initialized | 0 | [8 empty] | Battery is initialized. | The battery is correctly initialized.
|  | S065 - Battery Alive | 1 | [8 empty] | Battery is alive. | The communication with the battery is OK.
|  | S066 - Battery Ready | 2 | [8 empty] | Battery manager is ready. | The battery is powered up and ready to work.
|  | S067 - Battery Disconnection Request | 3 | [8 empty] | Battery disconnection request. | The battery is ordered to disconnect from the inverter.
|  | S068 - Battery Balancing | 4 | [8 empty] | Battery is balancing. | Some racks of the battery are balancing.
|  | S069 - Battery Charging | 5 | [8 empty] | Battery is charging. | The battery is charging.
|  | S070 - Battery Discharging | 6 | [8 empty] | Battery is discharging. | The battery is discharging.
|  | S071 - Battery in Sleep Mode (used on ME3 project) | 7
|  | S072 - N/A | 8
|  | S073 - Battery Performance Mode | 9 | [9 empty] | (Legacy)
|  | S074 - Battery Power Saving Mode | 10 | [9 empty] | (Legacy)
|  | S075 - N/A | 11
|  | S076 - N/A | 12
|  | S077 - N/A | 13
|  | S078 - N/A | 14
|  | S079 - N/A | 15
States Word 6
7 |  | SW6 |  |  | bitfield16 | [6 empty] | States Word 6 | States Word 6 |  |  |  | A319 | 41753
|  | S080 - ESS main load break switch closed | 0 | [9 empty] | (Legacy)
|  | S081 - CB-S opened | 1 | [8 empty] | ESS Circuit Breaker is opened. | The AC circuit-breaker or contactor of the ESS is opened.
|  | S082 - CB-S closed | 2 | [8 empty] | ESS Circuit Breaker is closed. | The AC circuit-breaker or contactor of the ESS is closed.
|  | S083 - CB-G opened | 3 | [8 empty] | Mains Circuit Breaker is opened. | The circuit-breaker from the Mains is opened.
|  | S084 - CB-G closed | 4 | [8 empty] | Mains Circuit Breaker is closed. | The circuit-breaker from the Mains is closed.
|  | S085 - Voltage detection on the comon busbar | 5 | [9 empty] | (Legacy)
|  | S086 - By-Pass in the position 0 | 6 | [9 empty] | (Legacy)
|  | S087 - By-Pass in the position 1 | 7 | [9 empty] | (Legacy)
|  | S088 - By-Pass in the position 2 | 8 | [9 empty] | (Legacy)
|  | S089 - Distribution cabinet AC circuit closed | 9 | [9 empty] | (Legacy)
|  | S090 - Distribution cabinet DC circuit closed | 10 | [9 empty] | (Legacy)
|  | S091 - Automatic mode selected | 11 | [8 empty] | ESS is in automatic mode. | (Legacy)
|  | S092 - Manual mode selected | 12 | [8 empty] | ESS is in manual mode. | (Legacy)
|  | S093 - Out Of Order mode selected | 13 | [8 empty] | ESS is in out of order mode. | The ESS is in out-of-order mode and cannot get connected.
|  | S094 - Reset push button | 14 | [8 empty] | Reset button is pressed. | (Legacy) The reset button is being pressed.
|  | S095 - Application Mode Enabled | 15 | [8 empty] | Custom application enabled. | The customized application is enabled in the settings.
States Word 7
8 |  | SW7 |  |  | bitfield16 | [6 empty] | States Word 7 | States Word 7 |  |  |  | A31A | 41754
|  | S096 - Genset main load break switch closed | 0 | [9 empty] | (Legacy)
|  | S097 - Renewable Energy main load break switch closed | 1 | [9 empty] | (Legacy)
|  | S098 - Back-up Genset main load break switch closed | 2 | [9 empty] | (Legacy)
|  | S099 - CB-R opened | 3 | [8 empty] | Renewables Circuit Breaker is opened. | The circuit-breaker of the Renewables source is opened.
|  | S100 - CB-R closed | 4 | [8 empty] | Renewables Circuit Breaker is closed. | The circuit-breaker of the Renewables source is closed.
|  | S101 - CB-GEN opened | 5 | [8 empty] | Genset Circuit Breaker is opened. | The circuit-breaker of the Genset source is opened.
|  | S102 - CB-GEN closed | 6 | [8 empty] | Genset Circuit Breaker is closed. | The circuit-breaker of the Genset source is closed.
|  | S103 - SPI Contactor Closed | 7 | [9 empty] | (Legacy)
|  | S104 - N/A | 8
|  | S105 - N/A | 9
|  | S106 - N/A | 10
|  | S107 - N/A | 11
|  | S108 - N/A | 12
|  | S109 - N/A | 13
|  | S110 - N/A | 14
|  | S111 - N/A | 15
States Word 8
9 |  | SW8 |  |  | bitfield16 | [6 empty] | States Word 8 | States Word 8 |  |  |  | A31B | 41755
|  | S112 - N/A | 0
|  | S113 - N/A | 1
|  | S114 - N/A | 2
|  | S115 - N/A | 3
|  | S116 - N/A | 4
|  | S117 - N/A | 5
|  | S118 - N/A | 6
|  | S119 - N/A | 7
|  | S120 - N/A | 8
|  | S121 - N/A | 9
|  | S122 - N/A | 10
|  | S123 - N/A | 11
|  | S124 - N/A | 12
|  | S125 - N/A | 13
|  | S126 - N/A | 14
|  | S127 - N/A | 15
10 |  | SW9 |  |  | bitfield16 | [6 empty] | States Word 9 | States Word 9 |  |  |  | A31C | 41756
11 |  | SW10 |  |  | bitfield16 | [6 empty] | States Word 10 | States Word 10 |  |  |  | A31D | 41757
12 |  | SW11 |  |  | bitfield16 | [6 empty] | States Word 11 | States Word 11 |  |  |  | A31E | 41758
13 |  | SW12 |  |  | bitfield16 | [6 empty] | States Word 12 | States Word 12 |  |  |  | A31F | 41759
14 |  | SW13 |  |  | bitfield16 | [6 empty] | States Word 13 | States Word 13 |  |  |  | A320 | 41760
15 |  | SW14 |  |  | bitfield16 | [6 empty] | States Word 14 | States Word 14 |  |  |  | A321 | 41761
16 |  | SW15 |  |  | bitfield16 | [6 empty] | States Word 15 | States Word 15 |  |  |  | A322 | 41762
17 |  | SW16 |  |  | bitfield16 | [6 empty] | States Word 16 | States Word 16 |  |  |  | A323 | 41763
Warnings Word 1
18 |  | WW1 |  |  | bitfield16 | [6 empty] | Warnings Word 1 | Warnings Word 1 |  |  |  | A324 | 41764
|  | W000 - General Warning | 0 | [8 empty] | General Warning. At least one Warning is active. | Troubleshooting : No action.
|  | W001 - Synchronization Not Completed | 1 | [8 empty] | Synchronization not completed. Synchronization phase aborted. | (Legacy) Applicable for Off-Grid Operations. Troubleshooting : No action, a new synchronization will start automatically.
|  | W002 - SOC out of range for OffGrid Mode | 2 | [8 empty] | SOC out of range for Off Grid Mode. The programmed transition from 'On-Grid Mode' to 'Off-Grid Mode' is not allowed because the battery SOC is out of range (too low or too high). | Applicable for Off-Grid Operations. Troubleshooting : Charge or discharge the battery (according to the situation) to allow transition to Off-Grid mode.
|  | W003 - Capability out of range for OffGrid Mode | 3 | [8 empty] | Capability out of Range for Off Grid Mode. The programmed transition from 'On-Grid Mode' to 'Off-Grid Mode' is not allowed because the system power is too low. | Applicable for Off-Grid Operations. Troubleshooting : Reduce the site consumption (load shedding) to allow transition to Off-Grid mode.
|  | W004 - Grid code relay alarm | 4
|  | W005 - EMS WatchDog Warning | 5 | [8 empty] | EMS WatchDog Warning. WatchDog timeout has elapsed: a failure has occurred in the communication link between the PMS and the EMS. This fault does not prevent the PMS from operating. | Troubleshooting : - Check that the EMS is still working and that it refreshes the watchdog. - Check that the communication cable between the EMS and the PMS is not damaged. - Check the setting of the 'Watchdog timeout' parameter and adjust if necessary according to the time needed by the EMS.
|  | W006 - SOC Very Low | 6 | [8 empty] | SOC Very low. Battery SOC is below 'SOC Very low' threshold. | Troubleshooting : Charge the battery.
|  | W007 - SOC Low | 7 | [8 empty] | SOC Low. Battery SOC is below 'SOC Low' threshold. | Troubleshooting : Charge the battery.
|  | W008 - SOC High | 8 | [8 empty] | SOC High. Battery SOC is over 'SOC High' threshold. | Troubleshooting : Discharge the battery.
|  | W009 - SOC Very High | 9 | [8 empty] | SOC Very High. Battery SOC is over 'SOC Very high' threshold. | Troubleshooting : Discharge the battery.
|  | W010 - ESS in maintenance | 10 | [8 empty] | ESS in maintenance Warning. The ESS has been left in maintenance mode. | Troubleshooting : Contact SOCOMEC service team.
|  | W011 - Application Warning Active -> GVL_App_Warning | 11 | [8 empty] | Customer Warning. The customized Warning is active. | Troubleshooting : Correct the fault, according to its setting.
|  | W012 - Version Compatibility Mismatch | 12 | [8 empty] | Version Compatibility Mismatch with at least one equipment. | Troubleshooting : firmware of concerned equipments must be upgraded.
|  | W013 - Microgrid Software Fuse Blown | 13 | [8 empty] | Microgrid Fuse Blown is detected by the software. | Troubleshooting : Check the connection with voltage sensing devices.
|  | W014 - N/A | 14
|  | W015 - Low Level of External PLC Battery | 15 | [8 empty] | PLC Battery Low Warning. The battery of the PLC is low. | Troubleshooting : Replace the battery.
Warnings Word 2
19 |  | WW2 |  |  | bitfield16 | [6 empty] | Warnings Word 2 | Warnings Word 2 |  |  |  | A325 | 41765
|  | W016 - Power Converters Warning | 0 | [8 empty] | Summary of Power Converters Warnings. A warning is present on at least one PCS. | Troubleshooting : Refer to the warning and do the linked action.
|  | W017 - At Least One PCS Warning Active | 1 | [8 empty] | PCS Warning. A warning is active on at least one PCS. | Troubleshooting : No action.
|  | W018 - At Least One PCS In Alarm State | 2 | [8 empty] | PCS Alarm. An alarm is active on at least one PCS, but the system is still operational. | Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W019 - At Least One PCS In Critical Alarm State | 3 | [8 empty] | A critical alarm is active on at least one PCS, but the system is still operational. | Troubleshooting : Contact SOCOMEC service team.
|  | W020 - AT Least One PCS Module In Alarm | 4 | [8 empty] | PCS module Alarm. An alarm is active on at least one PCS module, but the system is still operational. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W021 - At Least One PCS In Local Mode | 5 | [8 empty] | At least one PCS is operating in local mode via the HMI. | Troubleshooting : Put the PCS back in remote control mode so that the PMS can take control.
|  | W022 - At Least One PCS In Sleep Mode | 6 | [8 empty] | PCS in Sleep Mode. At least one PCS is in Sleep Mode. | (Legacy) Troubleshooting : No action, this mode exits automatically.
|  | W023 - At Least One PCS Maintenance Mode | 7 | [8 empty] | PCS in Maintenance Mode. At least one PCS is in Maintenance Mode. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
|  | W024 - Converters Parameters of PMS Are Changed | 8 | [8 empty] | Converters Parameters Changed. Main converters parameters of the PMS have changed. | Troubleshooting : Restart the complete system (including the auxiliaries).
|  | W025 - Lost Communication With At Least One PCS | 9 | [8 empty] | PCS Communication Loss. Communication lost with at least one PCS. | Troubleshooting : - Check the communication cable between the PMS and the PCS. - Restart the PCS (auxiliaries). - Notify SOCOMEC technical support if the problem lasts.
|  | W026 - C-Cab temperature | 10 | [8 empty] | C-Cabinet temperature high or Low Warning. The temperature of the control cabinet is over or under the warning alarm threshold. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | W027 - PCS Specific Warning | 11 | [8 empty] | PCS specific Warning. Warning linked to the currently set type of PCS. | Troubleshooting : Notify SOCOMEC technical support.
|  | W028 - N/A | 12
|  | W029 - Internal battery communication fault | 14 | [8 empty] | Battery Internal Communication Fault. There is an internal communication fault on the battery. | Troubleshooting : - Check the communication cables between the different racks and between the different modules of each rack. - Notify SOCOMEC technical support
|  | W030 - Battery Data Logger communication fault | 14 | [8 empty] | Battery Communication Loss. Communication lost with battery data logger. | Troubleshooting : Notify SOCOMEC technical support.
|  | W031 - Battery Data Logger is in fault state | 15 | [8 empty] | Battery data logger warning. Internal fault of battery data logger. | Troubleshooting : Notify SOCOMEC technical support.
Warnings Word 3
20 |  | WW3 |  |  | bitfield16 | [6 empty] | Warnings Word 3 | Warnings Word 3 |  |  |  | A326 | 41766
|  | W032 - Battery Warning | 0 | [8 empty] | Summary of Battery Warnings. At least one warning is present on the battery. | Troubleshooting : Refer to the warning and do the linked action.
|  | W033 - At least one Battery Rack in Alarm | 1 | [8 empty] | Battery rack Alarm. An active alarm is present on at least one battery rack, but the battery is still operational. | Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W034 - Battery Complete Discharged | 2 | [8 empty] | Battery fully discharged. The battery is fully discharged. | Troubleshooting : Charge the battery.
|  | W035 - At least one Battery Rack in Warning | 3 | [8 empty] | Battery rack Warning. A warning is present on at least one battery rack, but the battery is still operational. | Troubleshooting : No action.
|  | W036 - Battery Manual Mode Active | 4 | [8 empty] | Battery in Manual Mode. Manual control of the battery is enabled. | (Legacy) Troubleshooting : No action.
|  | W037 - Battery In Maintenance Mode | 5 | [8 empty] | Battery in Maintenance Mode. Battery is in 'Maintenance Mode'. | (Legacy) Troubleshooting : No action.
|  | W038 - Battery Parameters of PMS Are Changed | 6 | [8 empty] | Battery Parameters Changed. | Troubleshooting : Restart the complete system (including the auxiliaries).
|  | W039 - Battery Type is Changed | 7 | [8 empty] | Battery type change. Battery type setting has been changed. A restart of the PMS is needed to apply the change. | Troubleshooting : Restart the complete system (including the auxiliaries).
|  | W040 - Battery Over Voltage | 8 | [8 empty] | Battery Over Voltage. Battery voltage is high. | Troubleshooting : Notify SOCOMEC technical support.
|  | W041 - Battery Under Voltage | 9 | [8 empty] | Battery Under Voltage. Battery voltage is low. | Troubleshooting : Notify SOCOMEC technical support.
|  | W042 - Battery Cell Over Voltage | 10 | [8 empty] | Battery Cell Over Voltage. At least one cell voltage is high. | Troubleshooting : Notify SOCOMEC technical support.
|  | W043 - Battery Cell Under Voltage | 11 | [8 empty] | Battery Cell Under Voltage. At least one cell voltage is low. | Troubleshooting : Notify SOCOMEC technical support.
|  | W044 - Battery Over Current in Charge | 12 | [8 empty] | Battery Over Current In Charge. Battery current during charge is too high. | Troubleshooting : Notify SOCOMEC technical support.
|  | W045 - Battery High Temperature | 13 | [8 empty] | Battery High Temperature. Battery temperature is high. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | W046 - Battery Low Temperature | 14 | [8 empty] | Battery Low Temperature. Battery temperature is low. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | W047 - Battery Over Current in Discharge | 15 | [8 empty] | Battery Over Current In Discharge. Battery current during discharge is too high. | Troubleshooting : Notify SOCOMEC technical support.
Warnings Word 4
21 |  | WW4 |  |  | bitfield16 | [6 empty] | Warnings Word 4 | Warnings Word 4 |  |  |  | A327 | 41767
|  | W048 - Battery Specific Warning | 0 | [8 empty] | Battery specific Warning. Warning linked to the currently set type of battery. | Troubleshooting : Refer to the Modbus document dedicated to batteries.
|  | W049 - Battery Over Power in Charge | 1 | [8 empty] | Battery Over Power In Charge. Battery power is too high during charge. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
|  | W050 - Battery Over Power in Discharge | 2 | [8 empty] | Battery Over Power In Discharge. Battery power is too high during discharge. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
|  | W051 - Battery Operation Mode Fault | 3 | [8 empty] | Battery Operation Mode Fault. PMS has not been able to perform last operation mode selection. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
|  | W052 - Battery Requires a Maintenance Operation | 4 | [8 empty] | Battery Maintenance Request. Battery is requiring a maintenance operation. | Troubleshooting : Notify SOCOMEC technical support.
|  | W053 - Battery unbalanced warning | 5 | [8 empty] | Battery Unbalance Warning. The battery is operating with unbalanced phases. | Troubleshooting : Notify SOCOMEC technical support.
|  | W054 - Battery needs a SOC calibration | 6 | [8 empty] | Battery SOC Calibration. The battery is requiring a SOC calibration. | Troubleshooting : Notify SOCOMEC technical support if you do not know how to calibrate.
|  | W055 - Battery Current Imbalance Warning (used on ME3 project) | 7 | [9 empty] | (Legacy)
|  | W056 - Battery Voltage Imbalance Warning (used on ME3 project) | 8 | [9 empty] | (Legacy)
|  | W057 - Battery Current Limitation is in progress (used with CATL) | 9 | [8 empty] | Battery Current Limitation. The PMS is limiting the current allowed inside the battery due to overcurrent detection. | Troubleshooting : Wait for a few minutes. If the warning does not go away, try to lower the P setpoint.
|  | W058 - Battery Cooling System Warning | 10 | [8 empty] | Battery cooling system in fault | Troubleshooting : - Check battery cooling system.
|  | W059 - Battery Component Failure | 11 | [8 empty] | One or more internal battery component are in fault. | Troubleshooting : - Check the maintenance procedure. - Notify SOCOMEC technical support.
|  | W060 - Battery Critical Component Failure | 12 | [8 empty] | One or more internal battery component are in critical fault. | Troubleshooting : - Notify SOCOMEC technical support.
|  | W061 - IC configuration in progress | 13 | [8 empty] | IC Configuration is in progress. The islanding controller is waiting for settings. | Applicable for Off-Grid Operations. Troubleshooting : Make sure the islanding controller is connected and restart the system(auxiliaries included)
|  | W062 - SEL Communication Lost | 14 | [8 empty] | SEL communication fault | Troubleshooting : - Check ethernet cables between SEL and AC-CAB switch - Check ethernet cable between AC-CAB switch and C-CAB automation box
|  | W063 - PLC-IC Communication Lost | 15 | [8 empty] | IC Communication fault | Troubleshooting : - Check ethernet cables between IC and AC-CAB switch - Check ethernet cable between AC-CAB switch and C-CAB automation box
Warnings Word 5
22 |  | WW5 |  |  | bitfield16 | [6 empty] | Warnings Word 5 | Warnings Word 5 |  |  |  | A328 | 41768
|  | W064 - AT least one Digiware probes communication fault | 0 | [8 empty] | Digiware Communication Warning. At least one Digiware detects a communication fault. | Troubleshooting : - Check that all Digiware products are operational (green LED) - Check the condition of the Digiware communication cables. - Check the presence of the end-of-line plug on the last product.
|  | W065 - At least one PV inverter communication fault | 1 | [8 empty] | PV Inverter Communication Warning. A communication fault is active on at least one PV inverter. | (Legacy) Troubleshooting : - Check that the PV inverters are operational. - Check the condition of the communication cable between the PMS and the PV inverters.
|  | W066 - At least one GE communication fault | 2 | [8 empty] | Genset Communication Warning. A communication fault is active on at least one genset. | Troubleshooting : - Check that the genset controllers are operational. - Check the condition of the communication cable between the PMS and these controllers.
|  | W067 - At least one Renewable inverter communication fault | 3 | [8 empty] | Renewable Inverter Communication Warning. A communication fault is active on at least one renewable production inverter. | (Legacy) Troubleshooting : - Check that the inverters are operational. - Check the condition of the communication cable between the PMS and these inverters.
|  | W068 - N/A | 4
|  | W069 - At least one PV inverter Alarm | 5 | [8 empty] | PV Inverter Alarm. An alarm is active on at least one PV inverter. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W070 - At least one GE Alarm | 6 | [8 empty] | Genset Alarm. An alarm is active on at least one genset. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W071 - At least one Wind inverter alarm | 7 | [8 empty] | Renewable Inverter Alarm. An alarm is active on at least one renewable production inverter. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W072 - N/A | 8
|  | W073 - At least one PV inverter warning | 9 | [8 empty] | PV Inverter Warning. A warning is active on at least one PV inverter. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W074 - At least one GE warning | 10 | [8 empty] | Genset Inverter Warning. A warning is active on at least one genset. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W075 - At least one Wind inverter warning | 11 | [8 empty] | Renewable Inverter Warning. A warning is active on at least one renewable production inverter. | (Legacy) Troubleshooting : Identify the alarm and refer to the linked actions.
|  | W076 - Battery Temperature Deviation | 12 | [8 empty] | A temperature deviation have been dectected inside one or multiple racks. | Troubleshooting : - Check battery cooling system. - Notify SOCOMEC technical support.
|  | W077 - Battery Switch Open | 13 | [8 empty] | At least on rack switch is opened | Toubleshooting : - Close the main rack switch.
|  | W078 - N/A | 14
|  | W079 - N/A | 15
Warnings Word 6
23 |  | WW6 |  |  | bitfield16 | [6 empty] | Warnings Word 6 | Warnings Word 6 |  |  |  | A329 | 41769
|  | W080 - IMD Warning | 0 | [8 empty] | IMD Warning. The Insulation Monitoring Device detected a fault (Warning threshold). | Troubleshooting : - Check the insulation measure indicated by the IMD. - Analyse the installation to identify the ground fault. - Notify SOCOMEC technical support.
|  | W081 - 24VDC Power Supply A fault | 1 | [8 empty] | 24VDC Power Supply fault. The 24V power supply inside the control/command cabinet detects a fault. | Troubleshooting : Check and if necessary replace the 24Vdc power supply.
|  | W082 - N/A | 2
|  | W083 - UPS Alarm Synthesis Active | 3 | [8 empty] | UPS Warning. The UPS inside the control/command cabinet is faulty. | Troubleshooting : Check and if necessary replace the UPS.
|  | W084 - Intrusion in battery room | 4 | [8 empty] | Intrusion in battery room. The door of at least one battery cabinet is open. | Troubleshooting : Close the battery cabinet door.
|  | W085 - Intrusion in PCS room | 5 | [8 empty] | Intrusion in converter room. The door of the container converter room is open. | Troubleshooting : Close the battery room door.
|  | W086 - Control Cabinet door opened | 6 | [8 empty] | The door of the control cabinet is open. | Troubleshooting : Close the control cabinet door.
|  | W087 - PCS Grid Connection Fail | 7 | [8 empty] | PCS cannot connect to the grid | Troubleshooting : Check AC and DC Voltage.
|  | W088 - PCS Switch Open | 8 | [8 empty] | At least one C-Cab Switch is open | Troubleshooting : C-Cab main switches
|  | W089 - PCS Disabled | 9 | [8 empty] | PCS has been disabled. | Troubleshooting : Enable the PCS.
|  | W090 - Humidity Warning | 10 | [8 empty] | Cabinet humidity high Warning. The humidity of the control cabinet is over the warning alarm threshold. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | W091 - N/A | 11
|  | W092 - N/A | 12
|  | W093 - N/A | 13
|  | W094 - HVAC system is in warning state | 14 | [8 empty] | HVAC Warning. The container HVAC is faulty. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | W095 - Fire Security System is in warning state | 15 | [8 empty] | Fire safety system Warning. The container fire detection/extinction system is faulty. | Troubleshooting : Check the operation of the fire safety system (central, sensors ...).
Warnings Word 7
24 |  | WW7 |  |  | bitfield16 | [6 empty] | Warnings Word 7 | Warnings Word 7 |  |  |  | A32A | 41770
|  | W096 - N/A | 0
|  | W097 - N/A | 1
|  | W098 - N/A | 2
|  | W099 - N/A | 3
|  | W100 - N/A | 4
|  | W101 - N/A | 5
|  | W102 - N/A | 6
|  | W103 - N/A | 7
|  | W104 - N/A | 8
|  | W105 - N/A | 9
|  | W106 - N/A | 10
|  | W107 - N/A | 11
|  | W108 - PV 1 Disabled | 12
|  | W109 - PV 1 Power Limitation | 13
|  | W110 - PV 2 Disabled | 14
|  | W111 - PV 2 Power Limitation | 15
Warnings Word 8
25 |  | WW8 |  |  | bitfield16 | [6 empty] | Warnings Word 8 | Warnings Word 8 |  |  |  | A32B | 41771
|  | W112 - PV 3 Disabled | 0
|  | W113 - PV 3 Power Limitation | 1
|  | W114 - PV 4 Disabled | 2
|  | W115 - PV 4 Power Limitation | 3
|  | W116 - PV 5 Disabled | 4
|  | W117 - PV 5 Power Limitation | 5
|  | W118 - PV 6 Disabled | 6
|  | W119 - PV 6 Power Limitation | 7
|  | W120 - PV 7 Disabled | 8
|  | W121 - PV 7 Power Limitation | 9
|  | W122 - PV 8 Disabled | 10
|  | W123 - PV 8 Power Limitation | 11
|  | W124 - PV 9 Disabled | 12
|  | W125 - PV 9 Power Limitation | 13
|  | W126 - PV 10 Disabled | 14
|  | W127 - PV 10 Power Limitation | 15
26 |  | WW9 |  |  | bitfield16 | [6 empty] | Warnings Word 9 | Warnings Word 9 |  |  |  | A32C | 41772
27 |  | WW10 |  |  | bitfield16 | [6 empty] | Warnings Word 10 | Warnings Word 10 |  |  |  | A32D | 41773
28 |  | WW11 |  |  | bitfield16 | [6 empty] | Warnings Word 11 | Warnings Word 11 |  |  |  | A32E | 41774
29 |  | WW12 |  |  | bitfield16 | [6 empty] | Warnings Word 12 | Warnings Word 12 |  |  |  | A32F | 41775
30 |  | WW13 |  |  | bitfield16 | [6 empty] | Warnings Word 13 | Warnings Word 13 |  |  |  | A330 | 41776
31 |  | WW14 |  |  | bitfield16 | [6 empty] | Warnings Word 14 | Warnings Word 14 |  |  |  | A331 | 41777
32 |  | WW15 |  |  | bitfield16 | [6 empty] | Warnings Word 15 | Warnings Word 15 |  |  |  | A332 | 41778
33 |  | WW16 |  |  | bitfield16 | [6 empty] | Warnings Word 16 | Warnings Word 16 |  |  |  | A333 | 41779
Alarms Word 1
34 |  | AW1 |  |  | bitfield16 | [6 empty] | Alarms Word 1 | Alarms Word 1 |  |  |  | A334 | 41780
|  | A000 - General Alarm | 0 | [8 empty] | General Alarm. At least one alarm is active. | Troubleshooting : No action.
|  | A001 - IMD Fault | 1 | [8 empty] | IMD Alarm. Insulation Monitoring Device detected a fault(alarm threshold). | Troubleshooting : SOCOMEC technical support intervention is required to restart the system.
|  | A002 - EMS WatchDog Alarm | 2 | [8 empty] | EMS WatchDog Alarm. Watchdog timeout has elapsed: a failure occurred in the communication link between the PMS and the EMS. The PMS performs autonomous stop operations and all command bits as well as active - reactive power set points are automatically cleared. | Troubleshooting : - Check that the EMS is still working and that it refreshes the watchdog. - Check that the communication cable between the EMS and the PMS is not damaged.
|  | A003 - SoC out of range for Off-Grid | 3 | [8 empty] | SoC is lower than minimum SoC for islanding. If system is grid-forming, it has to be stopped to preserve batteries. Alarm is inhibited in On-Grid mode. | Troubleshooting : System must be restarted in On-Grid mode and batteries must be charged
|  | A004 - N/A | 4
|  | A005 - N/A | 5
|  | A006 - N/A | 6
|  | A007 - N/A | 7
|  | A008 - N/A | 8
|  | A009 - Transformer overheating | 9 | [8 empty] | Transformer overheating. The transformer inside the container is overheated. | Troubleshooting : Notify SOCOMEC technical support.
|  | A010 - External Emergency Alarm | 10 | [8 empty] | Emergency Stop Alarm. The Emergency Stop is active. | Troubleshooting : Check that everything is all right and disable the emergency stop.
|  | A011 - Application Alarm Active | 11 | [8 empty] | Customer Alarm. The customized Alarm is active. | Troubleshooting : Correct the alarm, according to its settings.
|  | A012 - N/A | 12
|  | A013 - Micro Grid Voltage Fault | 13 | [8 empty] | Micro Grid Voltage Fault. The micro grid voltage is out of range during an Off-Grid mode. | Troubleshooting : Check that the voltage level is compliant to the ranges (grid code...).
|  | A014 - Black Start Timeout Expired | 14 | [8 empty] | Blackstart Timeout Expired. The PMS has not completed the Blackstart procedure within the maximum period. | Applicable for Off-Grid Operations. Troubleshooting : Notify SOCOMEC technical support.
|  | A015 - PCS General Alarm | 15 | [8 empty] | At least One PCS module is in Alarm. | Check other alarm present in the system. If none are display notify SOCOMEC technical support.
Alarms Word 2
35 |  | AW2 |  |  | bitfield16 | [6 empty] | Alarms Word 2 | Alarms Word 2 |  |  |  | A335 | 41781
|  | A016 - Power Converters Fault | 0 | [8 empty] | Summary of Power Converters Alarms. An alarm is present on at least one PCS. | Troubleshooting : Refer to the alarm and do the linked action.
|  | A017 - Converters Watchdog Alarm | 1 | [8 empty] | PCS Watchdog Alarm. PCS Watchdog timeout elapsed. | Troubleshooting : Check the communication cable between the PMS and the PCS. Restart the PCS (auxiliaries). Notify SOCOMEC technical support if the problem persists.
|  | A018 - No PCSs Alive | 2 | [8 empty] | Lack of PCS. No PCS is detected on the communication network. | Troubleshooting : - Check the communication cable between the PMS and the PCS. - Check that the PCS auxiliaries are powered (push a button and check that the screen lights up).
|  | A019 - All PCSs in Alarm | 3 | [8 empty] | All PCS are in Alarm. An alarm is active on all PCS. | Troubleshooting : Refer to the alarms and do the linked action.
|  | A020 - Inverters Fault | 4 | [8 empty] | Inverter fault. An alarm is active on all PCS and at least one has an inverter fault. | Troubleshooting : Notify SOCOMEC technical support.
|  | A021 - Thermal Protection Fault | 5 | [8 empty] | Thermal Protection Fault. An alarm is active on all PCS and at least one has a thermal protection fault. | Troubleshooting : - Check/measure the conversion room temperature. - Check the operation of the cooling system (HVAC/fans...).
|  | A022 - Converters Critical Alarm | 6 | [8 empty] | PCS Critical Alarm. An alarm is active on all PCS and at least one has a critical alarm. | Troubleshooting : Notify SOCOMEC technical support.
|  | A023 - PCSs DC Disconnection Fault | 7 | [8 empty] | DC Disconnection Fault. There is a DC voltage on the PCS, even though the battery is disconnected. | Troubleshooting : Restart the battery auxiliaries. Notify SOCOMEC technical support if the problem persists or restarts.
|  | A024 - PCSs DC Connection Fault | 8 | [8 empty] | DC Connection Fault. There is no DC voltage on the PCS, even though the battery is connected. | Troubleshooting : Check that the different switches /circuit breakers of the DC bus are closed.
|  | A025 - PCSs Black Start Fault | 9 | [8 empty] | Blackstart Alarm. A fault of PCS management is detected during Blackstart process. | Troubleshooting : Notify SOCOMEC technical support.
|  | A026 - Environmental Conditions Not OK | 10 | [8 empty] | The PCS cannot power ON due to bad environmental conditions. | Troubleshooting : Wait for execution of the drying process.
|  | A027 - C-Cab temperature | 11 | [8 empty] | C-Cabinet temperature Alarm. The temperature of the control cabinet is over the alarm threshold. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A028 - Bus Coupler Communication Lost | 12 | [8 empty] | Bus Coupler Communication Fault | Troubleshooting : - Check ethernet cables between Bus Coupler and AC-CAB switch - Check ethernet cable between AC-CAB switch and C-CAB automation box - Check Bus Coupler Extension I/O Cards
|  | A029 - Battery Required a Maintenance Operation | 13 | [8 empty] | Battery Maintenance Alarm. A maintenance is required on the batteries. | Troubleshooting : Notify SOCOMEC technical support.
|  | A030 - Internal battery communication fault | 14 | [8 empty] | Battery Internal Communication Fault. There is an internal communication fault on the battery. | Troubleshooting : Check the communication cables between the different racks and between the different modules of each rack.
|  | A031 - Battery Gateway Communication Fault | 15 | [8 empty] | Battery Gateway Communication Fault. Communication fault between the CAN gateway and the battery BMS. | (Legacy) Troubleshooting : - Check the correct functioning of the CAN gateway (no red LED active). - Check the communication cable between the gateway and the PMS. - Restart the complete system (including the auxiliaries).
Alarms Word 3
36 |  | AW3 |  |  | bitfield16 | [6 empty] | Alarms Word 3 | Alarms Word 3 |  |  |  | A336 | 41782
|  | A032 - Battery Fault | 0 | [8 empty] | Summary of Battery Alarms. An alarm is present on at least one battery. | Troubleshooting : Refer to the warning and do the linked action.
|  | A033 - Battery Communication Fault | 1 | [8 empty] | Battery Communication Fault. Communication problem between the PMS and the battery BMS or gateway (if present). | Troubleshooting : - Check the communication cable between the battery and the PMS (or the gateway). - Restart the complete system (including the auxiliaries).
|  | A034 - Battery WatchDog Alarm | 2 | [8 empty] | Battery Watchdog Alarm. BMS Watchdog timeout elapsed. | Troubleshooting : - Check the communication cable between the battery and the PMS (or the gateway). - Restart the complete system (including the auxiliaries).
|  | A035 - Battery Initialization Fault | 3 | [8 empty] | Battery Initialization Fault. Initialization of the battery BMS failed. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
|  | A036 - Battery Over Voltage | 4 | [8 empty] | Battery Over Voltage. The battery voltage is critically high. | Troubleshooting : Notify SOCOMEC technical support.
|  | A037 - Battery Under Voltage | 5 | [8 empty] | Battery Under Voltage. The battery voltage is critically low. | Troubleshooting : Notify SOCOMEC technical support.
|  | A038 - Battery Over Charge Power | 6 | [8 empty] | Battery Over Power In Charge. The battery power is critically high during charge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A039 - Battery Over Discharge Power | 7 | [8 empty] | Battery Over Power In Discharge. The battery power is critically high during discharge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A040 - Battery Cell Over Voltage | 8 | [8 empty] | Battery Cell Over Voltage. The battery cell voltage is critically high. | Troubleshooting : Notify SOCOMEC technical support.
|  | A041 - Battery Cell Under Voltage | 9 | [8 empty] | Battery Cell Under Voltage. The battery cell voltage is critically low. | Troubleshooting : Notify SOCOMEC technical support.
|  | A042 - Battery Over Charge Current | 10 | [8 empty] | Battery Overcurrent In Charge. The battery current is critically high during charge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A043 - Battery Over Discharge Current | 11 | [8 empty] | Battery Overcurrent In Discharge. The battery current is critically high during discharge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A044 - Battery High Temperature | 12 | [8 empty] | Battery High Temperature. The battery temperature is critically high. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A045 - Battery Low Temperature | 13 | [8 empty] | Battery Low Temperature. The battery temperature is critically low. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A046 - Battery Disconnection Fault | 14 | [8 empty] | Battery Disconnection Fault. A fault of the battery management occurs during battery disconnection. | Troubleshooting : Notify SOCOMEC technical support.
|  | A047 - Battery Critical Alarm | 15 | [8 empty] | Battery Critical Alarm. A critical alarm is active on the battery. | (Legacy) Troubleshooting : Notify SOCOMEC technical support.
Alarms Word 4
37 |  | AW4 |  |  | bitfield16 | [6 empty] | Alarms Word 4 | Alarms Word 4 |  |  |  | A337 | 41783
|  | A048 - Battery SOC High | 0 | [8 empty] | SOC Safety High. The battery charge reaches 'SOC_Safety_High' threshold. | Troubleshooting : Notify SOCOMEC technical support.
|  | A049 - Battery SOC Low | 1 | [8 empty] | SOC Safety Low. The battery charge reaches 'SOC_Safety_Low' threshold. | Troubleshooting : Notify SOCOMEC technical support.
|  | A050 - Battery Connection Fault | 2 | [8 empty] | Battery Connection Fault. A fault of the battery management occurs during battery connection. | Troubleshooting : Notify SOCOMEC technical support.
|  | A051 - Battery Unbalanced Voltage Fault | 3 | [8 empty] | Battery Unbalanced. Battery fault due to an unbalanced voltage between racks during charge or discharge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A052 - Battery Ciruit Breakers Open | 4 | [8 empty] | Battery Circuit Breakers Open. All circuit breakers of battery racks are opened. | Troubleshooting : Close the circuit breakers on all racks.
|  | A053 - Battery Fans Out Of Order | 5 | [8 empty] | Battery Fans Out Of Order. All Battery Fans are out of order. | Troubleshooting : - Check that the power supply dedicated to fans still operates, if not replace it. - Identify faulty fans and replace them.
|  | A054 - Battery Specific Alarm | 6 | [8 empty] | Battery Specific Alarm. Battery alarm specific for the selected battery type. | Troubleshooting : Notify SOCOMEC technical support.
|  | A055 - Battery Management System Alarm | 7 | [8 empty] | BMS Alarm. Battery Management System in Alarm. | Troubleshooting : Notify SOCOMEC technical support.
|  | A056 - Battery All Battery Racks in Alarm | 8 | [8 empty] | Racks Alarm. An alarm is present on all battery racks. | Troubleshooting : Notify SOCOMEC technical support.
|  | A057 - Battery Unbalanced Current Fault | 9 | [8 empty] | Battery Current Unbalance. Battery fault due to an unbalanced current between racks during charge or discharge. | Troubleshooting : Notify SOCOMEC technical support.
|  | A058 - IC General Alarm | 10 | [8 empty] | Summary of Islanding Controller Alarms. At least one alarm is present on the islanding controller. | Applicable for Off-Grid Operations. Troubleshooting : Restart the islanding controller auxiliaries.
|  | A059 - IC Grid Phase Rotation | 11 | [8 empty] | Grid Phase Rotation. The islanding controller detected a wrong grid phase rotation. | Applicable for Off-Grid Operations. Troubleshooting : Check the phase rotation upstream and downstream of the CB-G.
|  | A060 - IC ESS Grid Phase Rotation | 12 | [8 empty] | Micro Grid Phase Rotation. The islanding controller detected a wrong micro grid phase rotation. | Applicable for Off-Grid Operations. Troubleshooting : Check the phase rotation upstream and downstream of the CB-G.
|  | A061 - IC Internal Fault | 13 | [8 empty] | Islanding Controller Fault. An internal fault is present in the islanding controller. | Applicable for Off-Grid Operations. Troubleshooting : Restart the islanding controller auxiliaries.
|  | A062 - IC-PLC Communication Lost | 14 | [8 empty] | Islanding Controller Communication Lost. Fault in communication detected by the islanding controller. | (Legacy) Applicable for Off-Grid Operations. Troubleshooting : Check the communication cable between the PMS and the islanding controller.
|  | A063 - PLC-IC Communication Lost | 15 | [8 empty] | PMS Communication Lost. Fault in communication detected by the PLC. | Applicable for Off-Grid Operations. Troubleshooting : Check the communication cable between the PMS and the islanding controller.
Alarms Word 5
38 |  | AW5 |  |  | bitfield16 | [6 empty] | Alarms Word 5 | Alarms Word 5 |  |  |  | A338 | 41784
|  | A064 - CB-S feedbacks mismatch | 0 | [8 empty] | CB-S Position Feedbacks. The storage circuit breaker position feedbacks are wrong. | (Legacy) Troubleshooting : Check the wiring of the CB-S position feedbacks.
|  | A065 - CB-S command fault | 1 | [8 empty] | CB-S Command Fault. Order and position feedbacks of the storage circuit breaker do not match. | (Legacy) Troubleshooting : - Check that the CB-S is in automatic mode. - Check the wiring of the circuit breaker controls (cables, relays, etc.). - Check the remote control power supply.
|  | A066 - CB-G feedbacks mismatch | 2 | [8 empty] | CB-G Position Feedbacks. The grid circuit breaker position feedbacks are wrong. | Applicable for Off-Grid Operations. Troubleshooting : Check the wiring of the CB-G position feedbacks.
|  | A067 - CB-G command fault | 3 | [8 empty] | CB-G Command Fault. Order and position feedbacks of the grid circuit breaker do not match. | Applicable for Off-Grid Operations. Troubleshooting : - Check that the CB-G is in automatic mode. - Check the wiring of the circuit breaker controls (cables, relays, etc.). - Check the remote control power supply.
|  | A068 - CB-R feedbacks mismatch | 4 | [8 empty] | CB-R Position Feedbacks. The renewable generator circuit breaker position feedbacks are wrong. | Troubleshooting : Check the wiring of the CB-R position feedbacks.
|  | A069 - CB-R command fault | 5 | [8 empty] | CB-G Command Fault. Order and position feedbacks of the renewable generator circuit breaker do not match. | Troubleshooting : - Check that the CB-R is in automatic mode. - Check the wiring of the circuit breaker controls (cables, relays, etc.). - Check the remote control power supply.
|  | A070 - CB-GEN feedbacks mismatch | 6 | [8 empty] | CB-GEN Position Feedbacks. The genset circuit breaker position feedbacks are wrong. | Applicable for Off-Grid Operations. Troubleshooting : Check the wiring of the CB-GEN position feedbacks.
|  | A071 - CB-GEN command fault | 7 | [8 empty] | CB-GEN Command Fault. Order and position feedbacks of the genset circuit breaker do not match. | Applicable for Off-Grid Operations. Troubleshooting : - Check that the CB-GEN is in automatic mode. - Check the wiring of the circuit breaker controls (cables, relays, etc.). - Check the remote control power supply.
|  | A072 - CB-Earthing feedbacks mismatch | 8 | [8 empty] | CB-Earthing Position Feedbacks. The earthing circuit breaker position feedbacks are wrong. | Applicable for Off-Grid Operations. Troubleshooting : Check the wiring of the CB-Earthing position feedbacks.
|  | A073 - CB-Earthing command fault | 9 | [8 empty] | CB-Earthing Command Fault. Order and position feedbacks of the earthing circuit breaker do not match. | Applicable for Off-Grid Operations. Troubleshooting : - Check that the CB-Earthing is in automatic mode. - Check the wiring of the circuit breaker controls (cables, relays, etc.). - Check the remote control power supply.
|  | A074 - CB-Earthing power supply fuse blown | 10 | [8 empty] | CB-Earthing Fuse Fault. Earthing circuit breaker power supply fuse blown. | Applicable for Off-Grid Operations. Troubleshooting : Replace the corresponding fuse.
|  | A075 - N/A | 11
|  | A076 - N/A | 12
|  | A077 - CB General fuse blown (used on ME3 project) | 13
|  | A078 - CB-GEN tripped | 14 | [8 empty] | CB- GEN Trip. The genset circuit breaker has tripped. | Applicable for Off-Grid Operations. Troubleshooting : Reset the circuit breaker once the tripping cause has been identified and corrected.
|  | A079 - CB-GEN power supply fuse blown | 15 | [8 empty] | CB-GEN Fuse Fault. Genset circuit breaker power supply fuse blown. | Applicable for Off-Grid Operations. Troubleshooting : Replace the corresponding fuse.
Alarms Word 6
39 |  | AW6 |  |  | bitfield16 | [6 empty] | Alarms Word 6 | Alarms Word 6 |  |  |  | A339 | 41785
|  | A080 - CB-S tripped | 0 | [8 empty] | CB-S Trip. The storage circuit breaker has tripped. | Troubleshooting : Reset the circuit breaker once the tripping cause has been identified and corrected.
|  | A081 - CB-S power supply fuse blown | 1 | [8 empty] | CB-S Fuse Fault. Storage circuit breaker power supply fuse blown. | Troubleshooting : Replace the corresponding fuse.
|  | A082 - CB-G tripped | 2 | [8 empty] | CB-G Trip. The grid circuit breaker has tripped. | Applicable for Off-Grid Operations. Troubleshooting : Reset the circuit breaker once the tripping cause has been identified and corrected.
|  | A083 - CB-G power supply fuse blown | 3 | [8 empty] | CB-G Fuse Fault. Grid circuit breaker power supply fuse blown. | Applicable for Off-Grid Operations. Troubleshooting : Replace the corresponding fuse.
|  | A084 - CB-R tripped | 4 | [8 empty] | CB-R Trip. The renewable generators circuit breaker has tripped. | Troubleshooting : Reset the circuit breaker once the tripping cause has been identified and corrected.
|  | A085 - CB-R power supply fuse blown | 5 | [8 empty] | CB-R Fuse Fault. Renewable generators circuit breaker power supply fuse blown. | Troubleshooting : Replace the corresponding fuse.
|  | A086 - Islanding controler voltage sensing upstream fuse blown | 6 | [8 empty] | Upstream islanding controller voltage sensor Fuse Fault. The upstream voltage sensor fuse inside the control/command cabinet blew. | Applicable for Off-Grid Operations. Troubleshooting : Replace the corresponding fuse.
|  | A087 - Islanding controler voltage sensing downstream fuse blown | 7 | [8 empty] | Downstream islanding controller voltage sensor Fuse Fault. The downstream voltage sensor fuse inside the control/command cabinet blew. | Applicable for Off-Grid Operations. Troubleshooting : Replace the corresponding fuse.
|  | A088 - Paralleling cabinet AC SPD fault | 8 | [8 empty] | Paralleling Cabinet AC SPD Fault. The AC surge protection device inside the paralleling cabinet is damaged. | (Legacy) Applicable for Off-Grid Operations. Troubleshooting : Replace or reset the protection.
|  | A089 - Distribution cabinet AC SPD fault | 9 | [8 empty] | Distribution Cabinet AC SPD Fault. The AC surge protection device inside the distribution cabinet is damaged. | Applicable for Off-Grid Operations. Troubleshooting : Replace or reset the protection.
|  | A090 - Distribution cabinet DC SPD fault | 10 | [8 empty] | Distribution Cabinet DC SPD Fault. The DC surge protection device inside the distribution cabinet is damaged. | (Legacy) Troubleshooting : Replace or reset the protection.
|  | A091 - Control cabinet AC SPD fault | 11 | [8 empty] | Control Cabinet AC SPD Fault. The AC surge protection device inside the control/command cabinet is damaged. | Troubleshooting : Replace or reset the protection.
|  | A092 - Container High Temperature Alarm (T > 40°C/104°F) | 12 | [8 empty] | Container High Temperature. The temperature inside the container is too high (T> 40 ° C / 104 ° F) | (Legacy) Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A093 - Cabinet High Humidity Alarm | 13 | [8 empty] | Cabinet High Humidity. The humidity inside the cabinet is too high. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A094 - HVAC system is in alarm state | 14 | [8 empty] | HVAC Alarm. An alarm is active on the container HVAC. | Troubleshooting : Check the operation of the heating / air conditioning system.
|  | A095 - Fire Security System is in alarm state | 15 | [8 empty] | Fire safety system alarm. An alarm is active on the container fire detection/extinction system. | Troubleshooting : Check the operation of the fire safety system (central, sensors, ...).
Alarms Word 7
40 |  | AW7 |  |  | bitfield16 | [6 empty] | Alarms Word 7 | Alarms Word 7 |  |  |  | A33A | 41786
|  | A096 - SEL Communication Lost | 0 | [8 empty] | SEL communication fault | Troubleshooting : - Check ethernet cables between SEL and AC-CAB switch - Check ethernet cable between AC-CAB switch and C-CAB automation box
|  | A097 - N/A | 1
|  | A098 - PCS Component Fault | 2 | [8 empty] | One or more PCS Component are in Fault | Troubleshooting : Check PCS maintenance procedure.
|  | A099 - PCS Specific Alarm | 3 | [8 empty] | PCS Specific Alarm. PCS alarm specific for the selected PCS type. | Troubleshooting : Notify SOCOMEC technical support.
|  | A100 - Current short-circuit alarm (used on ME3 project) | 4
|  | A101 - Battery param timeout (used on ME3 project) | 5
|  | A102 - PDU failure (used on ME3 project) | 6
|  | A103 - PDU lock (used on ME3 project) | 7
|  | A104 - Waiting init timestamp (used on ME3 project) | 8
|  | A105 - OV safety fuse triggered (used on ME3 project) | 9
|  | A106 - Data corrupted (used on ME3 project) | 10
|  | A107 - Precharge error (used on ME3 project) | 11
|  | A108 - Interlock error (used on ME3 project) | 12
|  | A109 - Var type mismatch (used on ME3 project) | 13
|  | A110 - Battery room intrusion (used on ME3 project) | 14
|  | A111 - Battery Temperature imbalanced (used on ME3 project) | 15
Alarms Word 8
41 |  | AW8 |  |  | bitfield16 | [6 empty] | Alarms Word 8 | Alarms Word 8 |  |  |  | A33B | 41787
|  | A112 - PCS Voltage Fault | 0 | [8 empty] | PCS Voltage are in criticial threshold. | Troubleshooting : - Measure and correct AC and DC voltage.
|  | A113 - PCS Overload | 1 | [8 empty] | One phase of the PCS is in overload. | Troubleshooting : - Correct the phase balance.
|  | A114 - N/A | 2
|  | A115 - N/A | 3
|  | A116 - N/A | 4
|  | A117 - N/A | 5
|  | A118 - N/A | 6
|  | A119 - N/A | 7
|  | A120 - N/A | 8
|  | A121 - N/A | 9
|  | A122 - N/A | 10
|  | A123 - N/A | 11
|  | A124 - N/A | 12
|  | A125 - N/A | 13
|  | A126 - N/A | 14
|  | A127 - N/A | 15
42 |  | AW9 |  |  | bitfield16 | [6 empty] | Alarms Word 9 | Alarms Word 9 |  |  |  | A33C | 41788
43 |  | AW10 |  |  | bitfield16 | [6 empty] | Alarms Word 10 | Alarms Word 10 |  |  |  | A33D | 41789
44 |  | AW11 |  |  | bitfield16 | [6 empty] | Alarms Word 11 | Alarms Word 11 |  |  |  | A33E | 41790
45 |  | AW12 |  |  | bitfield16 | [6 empty] | Alarms Word 12 | Alarms Word 12 |  |  |  | A33F | 41791
46 |  | AW13 |  |  | bitfield16 | [6 empty] | Alarms Word 13 | Alarms Word 13 |  |  |  | A340 | 41792
47 |  | AW14 |  |  | bitfield16 | [6 empty] | Alarms Word 14 | Alarms Word 14 |  |  |  | A341 | 41793
48 |  | AW15 |  |  | bitfield16 | [6 empty] | Alarms Word 15 | Alarms Word 15 |  |  |  | A342 | 41794
49 |  | AW16 |  |  | bitfield16 | [6 empty] | Alarms Word 16 | Alarms Word 16 |  |  |  | A343 | 41795

## 64902
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | SUNSYS HES-L | SUNSYS HES-XL | SUNSYS HES-XXL | HEX Address | DEC Address
|  | socomec_pms_islanding |  |  | group | [6 empty] | Socomec PMS islanding | Vendor model providing PMS commands for off grid features
0 |  | ID | 64902 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier |  |  |  | A344 | 41796
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length |  |  |  | A345 | 41797
2 |  | BlackStart_Ena |  |  | enum16 |  |  |  | RW |  |  | Black Start Enable |  |  |  |  | A346 | 41798
|  | Disable | 0
|  | Enable | 1
3 |  | UnplannedIsl_Ena |  |  | enum16 |  |  |  | RW |  |  | Unplanned Islanding Enable |  |  |  |  | A347 | 41799
|  | Disable | 0
|  | Enable | 1
4 |  | PlannedIsl_Rqst |  |  | enum16 |  |  |  | RW |  |  | Planned Islanding Request |  |  |  |  | A348 | 41800
|  | Disable | 0
|  | Enable | 1

## 707 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERTripLV |  |  | group | [6 empty] | DER Trip LV | DER low voltage trip model.
0 |  | ID | 707 |  | uint16 |  |  |  |  | M | S | Model ID | DER low voltage trip model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER low voltage trip model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip LV Module Enable | DER low voltage trip control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1.
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported.
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
7 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points.
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripLV.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLV.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve.
|  | DERTripLV.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLV.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripLV.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLV.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLV.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 708 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERTripHV |  |  | group | [6 empty] | DER Trip HV | DER high voltage trip model.
0 |  | ID | 708 |  | uint16 |  |  |  |  | M | S | Model ID | DER high voltage trip model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER high voltage trip model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip HV Module Enable | DER high voltage trip control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1.
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported.
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
7 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points.
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripHV.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHV.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve.
|  | DERTripHV.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHV.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripHV.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHV.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHV.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | V |  |  | uint16 |  | V_SF | VRefPct | RW |  |  | Voltage Point | Curve voltage point as percentage.
| 1 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 709 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERTripLF |  |  | group | [6 empty] | DER Trip LF | DER low frequency trip model.
0 |  | ID | 709 |  | uint16 |  |  |  |  | M | S | Model ID | DER low frequency trip model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER low frequency trip model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip LF Module Enable | DER low frequency trip control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1.
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported.
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
7 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Scale Factor | Scale factor for curve frequency points.
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripLF.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripLF.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve.
|  | DERTripLF.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLF.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripLF.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripLF.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripLF.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 710 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERTripHF |  |  | group | [6 empty] | DER Trip HF | DER high frequency trip model.
0 |  | ID | 710 |  | uint16 |  |  |  |  | M | S | Model ID | DER high frequency trip model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER high frequency trip model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Trip HF Module Enable | DER high frequency trip control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Adopt Curve Request | Index of curve points to adopt. First curve index is 1.
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Adopt Curve Result | Result of last adopt curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported.
6 |  | NCrvSet |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
7 |  | Hz_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Scale Factor | Scale factor for curve frequency points.
8 |  | Tms_SF |  |  | sunssf |  |  |  |  | M | S | Time Point Scale Factor | Scale factor for curve time points.
Stored curve sets - Number of curve sets contained in NCrvSet - The first set is read-only and indicates the current settings.
|  | DERTripHF.Crv |  | NCrvSet | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve set containing a Must Trip, May Trip, and Momentary Cessation Curve - Number of curve points contained in NPt
|  | DERTripHF.Crv.MustTrip |  |  | group | [6 empty] | Must Trip Curve | Stored must trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in must trip curve.
|  | DERTripHF.Crv.MustTrip.Pt |  | NPt | group | [6 empty] | Must Trip Curve Points | Must trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHF.Crv.MayTrip |  |  | group | [6 empty] | May Trip Curve | Stored may trip curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in may trip curve.
|  | DERTripHF.Crv.MayTrip.Pt |  | NPt | group | [6 empty] | May Trip Curve Points | May trip curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.
|  | DERTripHF.Crv.MomCess |  |  | group | [6 empty] | Momentary Cessation Curve | Stored momentary cessation curve.
| 0 | ActPt |  |  | uint16 |  |  |  | RW |  |  | Number Of Active Points | Number of active points in the momentary cessation curve.
|  | DERTripHF.Crv.MomCess.Pt |  | NPt | group | [6 empty] | Mom Cessation Curve Points | Momentary cessation curve points.
| 0 | Hz |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Frequency Point | Curve frequency point.
| 2 | Tms |  |  | uint32 |  | Tms_SF | Secs | RW |  |  | Time Point | Curve time point in seconds.

## 711 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERFreqDroop |  |  | group | [6 empty] | DER Frequency Droop | DER Frequency Droop model.
0 |  | ID | 711 |  | uint16 |  |  |  |  | M | S | Model ID | DER Frequency Droop model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Frequency Droop model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Frequency Droop Module Enable | DER Frequency-Watt (Frequency-Droop) control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCtlReq |  |  | uint16 |  |  |  | RW | M |  | Set Active Control Request | Set active control. 0 = No active control.
4 |  | AdptCtlRslt |  |  | enum16 |  |  |  |  | M |  | Set Active Control Result | Result of last set active control operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Control update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Control update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Control update failed.
5 |  | NCtl |  |  | uint16 |  |  |  |  | M | S | Stored Control Count | Number of stored controls supported.
6 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
8 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Left | Reversion time remaining in seconds.
10 |  | RvrtCtl |  |  | uint16 |  |  |  | RW |  |  | Reversion Control | Default control after reversion timeout.
11 |  | Db_SF |  |  | sunssf |  |  |  |  | M | S | Deadband Scale Factor | Deadband scale factor.
12 |  | K_SF |  |  | sunssf |  |  |  |  | M | S | Frequency Change Scale Factor | Frequency change scale factor.
13 |  | RspTms_SF |  |  | sunssf |  |  |  |  | M | S | Open-Loop Scale Factor | Open loop response time scale factor.
Stored control sets - Number of control sets contained in NCtl - The first set is read-only and indicates the current settings.
|  | DERFreqDroop.Ctl |  | NCtl | group | [6 empty] | Stored Controls | Stored control sets.
| 0 | DbOf |  |  | uint32 |  | Db_SF | Hz | RW | M |  | Over-Frequency Deadband | The deadband value for over-frequency conditions in Hz.
| 2 | DbUf |  |  | uint32 |  | Db_SF | Hz | RW | M |  | Under-Frequency Deadband | The deadband value for under-frequency conditions in Hz.
| 4 | KOf |  |  | uint16 |  | K_SF |  | RW | M |  | Over-Frequency Change Ratio | Frequency droop per-unit frequency change for over-frequency conditions corresponding to 1 per-unit power output change.
| 5 | KUf |  |  | uint16 |  | K_SF |  | RW | M |  | Under-Frequency Change Ratio | Frequency droop per-unit frequency change for under-frequency conditions corresponding to 1 per-unit power output change.
| 6 | RspTms |  |  | uint32 |  | RspTms_SF | Secs | RW | M |  | Open-Loop Response Time | The open-loop response time in seconds.
| 8 | PMin |  |  | int16 |  |  | Pct | RW |  |  | Minimum Active Power | The minimum active power output due to DER prime mover constraints, in percent of the DER active power rating. The valid range is -100 to 100. This setting applies only to the frequency droop control.
| 9 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Control Access | Control read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Control has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Control has read-only access.

## 712 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERWattVar |  |  | group | [6 empty] | DER Watt-Var | DER Watt-Var model.
0 |  | ID | 712 |  | uint16 |  |  |  |  | M | S | Model ID | DER Watt-Var model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Watt-Var model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | DER Watt-Var Module Enable | DER Watt-Var control enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M | S | Set Active Curve Request | Set active curve. 0 = No active curve.
4 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M | S | Set Active Curve Result | Result of last set active curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
5 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number Of Points | Number of curve points supported.
6 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
7 |  | RvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reversion Timeout | Reversion time in seconds. 0 = No reversion time.
9 |  | RvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reversion Time Left | Reversion time remaining in seconds.
11 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion Curve | Default curve after reversion timeout.
12 |  | W_SF |  |  | sunssf |  |  |  |  | M | S | Active Power Scale Factor | Scale factor for curve active power points.
13 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Var Scale Factor | Scale factor for curve var points.
Stored curve sets - Number of curve sets contained in NCrv - The first set is read-only and indicates the current settings.
|  | DERWattVar.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference.
|  | W_MAX_PCT | 0 | [8 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 1 | [8 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 2 | [8 empty] | Percent Available Vars
|  | VA_MAX_PCT | 3 | [8 empty] | Percent Max Apparent Power
| 2 | Pri |  |  | enum16 |  |  |  | RW |  |  | Power Priority | Power priority.
|  | ACTIVE | 0 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 1 | [8 empty] | Reactive Power Priority | Reactive power priority.
| 3 | ReadOnly |  |  | enum16 |  |  |  |  | M | S | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored curve sets - curve points for each stored curve - Number of curve points contained in NPt
|  | DERWattVar.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | W |  |  | int16 |  | W_SF | WMaxPct | RW |  |  | Active Power Point | Curve active power point as percentage.
| 1 | Var |  |  | int16 |  | DeptRef_SF | VarPct | RW |  |  | Reactive Power Point | Curve reactive power point as set in DeptRef point.

## 714 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | DERMeasureDC |  |  | group | [6 empty] | DER DC Measurement | DER DC measurement.
0 |  | ID | 714 |  | uint16 |  |  |  |  | M | S | Model ID | DER DC measurement model ID.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER DC measurement model length.
DC General
2 |  | PrtAlrms |  |  | bitfield32 | [6 empty] | Port Alarms | Bitfield of ports with active alarms. Bit is 1 if port has an active alarm. Bit 0 is first port.
4 |  | NPrt |  |  | uint16 | [5 empty] | S | Number Of Ports | Number of DC ports.
5 |  | DCA |  |  | int16 |  | DCA_SF |  |  |  |  | DC Current | Total DC current for all ports.
6 |  | DCW |  |  | int16 |  | DCW_SF |  |  |  |  | DC Power | Total DC power for all ports.
7 |  | DCWhInj |  |  | uint64 |  | DCWH_SF |  |  |  |  | DC Energy Injected | Total cumulative DC energy injected for all ports.
11 |  | DCWhAbs |  |  | uint64 |  | DCWH_SF |  |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for all ports.
15 |  | DCA_SF |  |  | sunssf | [5 empty] | S | DC Current Scale Factor | DC current scale factor.
16 |  | DCV_SF |  |  | sunssf | [5 empty] | S | DC Voltage Scale Factor | DC voltage scale factor.
17 |  | DCW_SF |  |  | sunssf | [5 empty] | S | DC Power Scale Factor | DC power scale factor.
18 |  | DCWH_SF |  |  | sunssf | [5 empty] | S | DC Energy Scale Factor | DC energy scale factor.
19 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature Scale Factor.
DC Port
|  | DERMeasureDC.Prt |  | NPrt | group
| 0 | PrtTyp |  |  | enum16 | [6 empty] | Port Type | Port type.
|  | PV | 0 | [8 empty] | Photovoltaic
|  | ESS | 1 | [8 empty] | Energy Storage System
|  | EV | 2 | [8 empty] | Electric Vehicle
|  | INJ | 3 | [8 empty] | Generic Injecting
|  | ABS | 4 | [8 empty] | Generic Absorbing
|  | BIDIR | 5 | [8 empty] | Generic Bidirectional
|  | DC_DC | 6 | [8 empty] | DC to DC
| 1 | ID |  |  | uint16 | [6 empty] | Port ID | Port ID.
| 2 | IDStr |  |  | string | 8 | [5 empty] | Port ID String | Port ID string.
| 10 | DCA |  |  | int16 |  | DCA_SF |  |  |  |  | DC Current | DC current for the port.
| 11 | DCV |  |  | uint16 |  | DCV_SF |  |  |  |  | DC Voltage | DC voltage for the port.
| 12 | DCW |  |  | int16 |  | DCW_SF |  |  |  |  | DC Power | DC power for the port.
| 13 | DCWhInj |  |  | uint64 |  | DCWH_SF |  |  |  |  | DC Energy Injected | Total cumulative DC energy injected for the port.
| 17 | DCWhAbs |  |  | uint64 |  | DCWH_SF |  |  |  |  | DC Energy Absorbed | Total cumulative DC energy absorbed for the port.
| 21 | Tmp |  |  | int16 | [6 empty] | DC Port Temperature | DC port temperature.
| 22 | DCSta |  |  | enum16 | [6 empty] | DC Port Status | DC port status.
|  | OFF | 0 | [8 empty] | Off
|  | ON | 1 | [8 empty] | On
|  | WARNING | 2 | [8 empty] | Warning
|  | ERROR | 3 | [8 empty] | Error
| 23 | DCAlrm |  |  | bitfield32 | [6 empty] | DC Port Alarm | DC port alarm.
|  | GROUND_FAULT | 0 | [8 empty] | Ground Fault
|  | INPUT_OVER_VOLTAGE | 1 | [8 empty] | Input Over Voltage
|  | DC_DISCONNECT | 3 | [8 empty] | DC Disconnect
|  | CABINET_OPEN | 5 | [8 empty] | Cabinet Open
|  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual Shutdown
|  | OVER_TEMP | 7 | [8 empty] | Over Temperature
|  | BLOWN_FUSE | 12 | [8 empty] | Blown Fuse
|  | UNDER_TEMP | 13 | [8 empty] | Under Temperature
|  | MEMORY_LOSS | 14 | [8 empty] | Memory Loss
|  | ARC_DETECTION | 15 | [8 empty] | Arc Detection
|  | RESERVED | 19 | [8 empty] | Reserved
|  | TEST_FAILED | 20 | [8 empty] | Test Failed
|  | INPUT_UNDER_VOLTAGE | 21 | [8 empty] | Under Voltage
|  | INPUT_OVER_CURRENT | 22 | [8 empty] | Over Current

## 804 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lithium_ion_string |  |  | group | [6 empty] | Lithium-Ion String Model
0 |  | ID | 804 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Idx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string within the bank.
3 |  | NMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Count of modules in the string.
4 |  | St |  |  | bitfield32 |  |  |  |  | M |  | String Status | Current status of the string.
|  | STRING_ENABLED | 0
|  | CONTACTOR_STATUS | 1
6 |  | ConFail |  |  | enum16 | [6 empty] | Connection Failure Reason
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | STR_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | STRING_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | STRING_FAULT | 8
7 |  | NCellBal |  |  | uint16 | [6 empty] | String Cell Balancing Count | Number of cells currently being balanced in the string.
8 |  | SoC |  |  | uint16 |  | SoC_SF | % |  | M |  | String State of Charge | Battery string state of charge, expressed as a percentage.
9 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | String Depth of Discharge | Depth of discharge for the string, expressed as a percentage.
10 |  | NCyc |  |  | uint32 | [6 empty] | String Cycle Count | Number of discharge cycles executed upon the string.
12 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | String State of Health | Battery string state of health, expressed as a percentage.
13 |  | A |  |  | int16 |  | A_SF | A |  | M |  | String Current | String current measurement.
14 |  | V |  |  | uint16 |  | V_SF | V |  |  |  | String Voltage | String voltage measurement.
15 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the string.
16 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with maximum cell voltage.
17 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the string.
18 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with minimum cell voltage.
19 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the string.
20 |  | ModTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Module Temperature | Maximum temperature for all modules in the string.
21 |  | ModTmpMaxMod |  |  | uint16 |  |  |  |  | M |  | Max Module Temperature Module | Module with the maximum temperature.
22 |  | ModTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Module Temperature | Minimum temperature for all modules in the string.
23 |  | ModTmpMinMod |  |  | uint16 |  |  |  |  | M |  | Min Module Temperature Module | Module with the minimum temperature.
24 |  | ModTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Module Temperature | Average temperature for all modules in the string.
25 |  | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
26 |  | ConSt |  |  | bitfield32 | [6 empty] | Contactor Status | Status of the contactor(s) for the string.
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
28 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_1 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_2 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
30 |  | Evt2 |  |  | bitfield32 | [6 empty] | String Event 2 | Alarms, warnings and status values. Bit flags.
32 |  | EvtVnd1 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 1 | Vendor defined events.
34 |  | EvtVnd2 |  |  | bitfield32 | [6 empty] | Vendor Event Bitfield 2 | Vendor defined events.
36 |  | SetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable String | Enables and disables the string. Should reset to 0 upon completion.
37 |  | SetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect String | Connects and disconnects the string.
|  | CONNECT_STRING | 1
|  | DISCONNECT_STRING | 2
38 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string state of charge.
39 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for string state of health.
40 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for string depth of discharge.
41 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for string current.
42 |  | V_SF |  |  | sunssf | [7 empty] | Scale factor for string voltage.
43 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
44 |  | ModTmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperature.
45 |  | Pad2 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
46 |  | Pad3 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
47 |  | Pad4 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
|  | lithium_ion_string.lithium_ion_string_module |  | 0 | group
| 0 | ModNCell |  |  | uint16 |  |  |  |  | M |  | Module Cell Count | Count of all cells in the module.
| 1 | ModSoC |  |  | uint16 |  | SoC_SF | % |  |  |  | Module SoC | Module state of charge, expressed as a percentage.
| 2 | ModSoH |  |  | uint16 |  | SoH_SF | % |  |  |  | Module SoH | Module state of health, expressed as a percentage.
| 3 | ModCellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the module.
| 4 | ModCellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with maximum voltage.
| 5 | ModCellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the module.
| 6 | ModCellVMinCell |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage Cell | Cell with minimum voltage.
| 7 | ModCellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the module.
| 8 | ModCellTmpMax |  |  | int16 |  | ModTmp_SF | C |  | M |  | Max Cell Temperature | Maximum temperature for all cells in the module.
| 9 | ModCellTmpMaxCell |  |  | uint16 | [6 empty] | Max Cell Temperature Cell | Cell with maximum temperature.
| 10 | ModCellTmpMin |  |  | int16 |  | ModTmp_SF | C |  | M |  | Min Cell Temperature | Minimum temperature for all cells in the module.
| 11 | ModCellTmpMinCell |  |  | uint16 | [6 empty] | Min Cell Temperature Cell | Cell with minimum temperature.
| 12 | ModCellTmpAvg |  |  | int16 |  | ModTmp_SF | C |  | M |  | Average Cell Temperature | Average temperature for all cells in the module.
| 13 | Pad5 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
| 14 | Pad6 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
| 15 | Pad7 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.

## 805 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | lithium-ion-module |  |  | group | [6 empty] | Lithium-Ion Module Model
0 |  | ID | 805 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | StrIdx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string containing the module.
3 |  | ModIdx |  |  | uint16 |  |  |  |  | M |  | Module Index | Index of the module within the string.
4 |  | NCell |  |  | uint16 |  |  |  |  | M |  | Module Cell Count | Count of all cells in the module.
5 |  | SoC |  |  | uint16 |  | SoC_SF | % |  |  |  | Module SoC | Module state of charge, expressed as a percentage.
6 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge for the module.
7 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | Module SoH | Module state of health, expressed as a percentage.
8 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Count of cycles executed.
10 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | Module Voltage | Voltage of the module.
11 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the module.
12 |  | CellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with the maximum voltage.
13 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the module.
14 |  | CellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with the minimum voltage.
15 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the module.
16 |  | CellTmpMax |  |  | int16 |  | Tmp_SF | C |  | M |  | Max Cell Temperature | Maximum temperature for all cells in the module.
17 |  | CellTmpMaxCell |  |  | uint16 | [6 empty] | Max Cell Temperature Cell | Cell with the maximum cell temperature.
18 |  | CellTmpMin |  |  | int16 |  | Tmp_SF | C |  | M |  | Min Cell Temperature | Minimum temperature for all cells in the module.
19 |  | CellTmpMinCell |  |  | uint16 | [6 empty] | Min Cell Temperature Cell | Cell with the minimum cell temperature.
20 |  | CellTmpAvg |  |  | int16 |  | Tmp_SF | C |  | M |  | Average Cell Temperature | Average temperature for all cells in the module.
21 |  | NCellBal |  |  | uint16 | [6 empty] | Balanced Cell Count | Number of cells currently being balanced in the module.
22 |  | SN |  |  | string | 16 | [5 empty] | Serial Number | Serial number for the module.
38 |  | SoC_SF |  |  | sunssf | [7 empty] | Scale factor for module state of charge.
39 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for module state of health.
40 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for module depth of discharge.
41 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module voltage.
42 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
43 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperature.
|  | lithium-ion-module.lithium-ion-module-cell |  | 0 | group
| 0 | CellV |  |  | uint16 |  | CellV_SF | V |  | M |  | Cell Voltage | Cell terminal voltage.
| 1 | CellTmp |  |  | int16 |  | Tmp_SF | C |  | M |  | Cell Temperature | Cell temperature.
| 2 | CellSt |  |  | bitfield32 | [6 empty] | Cell Status | Status of the cell.
|  | CELL_IS_BALANCING | 0

## 806 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | flow_battery |  |  | group | [6 empty] | Flow Battery Model
0 |  | ID | 806 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | BatTBD |  |  | uint16 |  |  |  |  | M |  | Battery Points To Be Determined
|  | flow_battery.battery_string |  | 0 | group
| 0 | BatStTBD |  |  | uint16 |  |  |  |  | M |  | Battery String Points To Be Determined

## 807 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | flow_battery_string |  |  | group | [6 empty] | Flow Battery String Model
0 |  | ID | 807 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Idx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string within the bank.
3 |  | NMod |  |  | uint16 |  |  |  |  | M |  | Module Count | Number of modules in this string.
4 |  | NModCon |  |  | uint16 |  |  |  |  | M |  | Connected Module Count | Number of electrically connected modules in this string.
5 |  | ModVMax |  |  | uint16 |  | ModV_SF | V |  | M |  | Max Module Voltage | Maximum voltage for all modules in the string.
6 |  | ModVMaxMod |  |  | uint16 | [6 empty] | Max Module Voltage Module | Module with the maximum voltage.
7 |  | ModVMin |  |  | uint16 |  | ModV_SF | V |  | M |  | Min Module Voltage | Minimum voltage for all modules in the string.
8 |  | ModVMinMod |  |  | uint16 | [6 empty] | Min Module Voltage Module | Module with the minimum voltage.
9 |  | ModVAvg |  |  | uint16 |  | ModV_SF | V |  | M |  | Average Module Voltage | Average voltage for all modules in the string.
10 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Max Cell Voltage | Maximum voltage for all cells in the string.
11 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with the maximum voltage.
12 |  | CellVMaxStk |  |  | uint16 | [6 empty] | Max Cell Voltage Stack | Stack containing the cell with the maximum voltage.
13 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage | Minimum voltage for all cells in the string.
14 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with the minimum voltage.
15 |  | CellVMinStk |  |  | uint16 | [6 empty] | Min Cell Voltage Stack | Stack containing the cell with the minimum voltage.
16 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average voltage for all cells in the string.
17 |  | TmpMax |  |  | int16 |  | Tmp_SF | C |  | M |  | Max Temperature | Maximum electrolyte temperature for all modules in the string.
18 |  | TmpMaxMod |  |  | uint16 | [6 empty] | Max Temperature Module | Module with the maximum temperature.
19 |  | TmpMin |  |  | int16 |  | Tmp_SF | C |  | M |  | Min Temperature | Minimum electrolyte temperature for all modules in the string.
20 |  | TmpMinMod |  |  | uint16 | [6 empty] | Min Temperature Module | Module with the minimum temperature.
21 |  | TmpAvg |  |  | int16 |  | Tmp_SF | C |  | M |  | Average Temperature | Average electrolyte temperature for all modules in the string.
22 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | String Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | RESERVED_1 | 18
|  | RESERVED_2 | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_3 | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | FIRE_ALARM | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
24 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | String Event 2 | Alarms, warnings and status values. Bit flags.
|  | LEAK_ALARM | 0
|  | PUMP_ALARM | 1
|  | HIGH_PRESSURE_ALARM | 2
|  | HIGH_PRESSURE_WARNING | 3
|  | LOW_FLOW_ALARM | 4
|  | LOW_FLOW_WARNING | 5
26 |  | EvtVnd1 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 1 | Vendor defined events.
28 |  | EvtVnd2 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 2 | Vendor defined events.
30 |  | ModV_SF |  |  | sunssf |  |  |  |  | M
31 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for voltage.
32 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for temperature.
33 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for state of charge.
34 |  | OCV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for open circuit voltage.
35 |  | Pad1 |  |  | pad |  |  |  |  | M |  | Pad | Pad register.
|  | flow_battery_string.module |  | 0 | group
| 0 | ModIdx |  |  | uint16 |  |  |  |  | M |  | Module Index | Index of the module within the string.
| 1 | ModNStk |  |  | uint16 |  |  |  |  | M |  | Stack Count | Number of stacks in this module.
| 2 | ModSt |  |  | bitfield32 |  |  |  |  | M |  | Module Status | Current status of the module.
|  | MODULE_ENABLED | 0
|  | CONTACTOR_STATUS | 1
| 4 | ModSoC |  |  | uint16 |  | SoC_SF | % |  | M |  | Module State of Charge | State of charge for this module.
| 5 | ModOCV |  |  | uint16 |  | OCV_SF | V |  | M |  | Open Circuit Voltage | Open circuit voltage for this module.
| 6 | ModV |  |  | uint16 |  | ModV_SF | V |  | M |  | External Voltage | External voltage fo this module.
| 7 | ModCellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Maximum Cell Voltage | Maximum voltage for all cells in this module.
| 8 | ModCellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with the maximum cell voltage.
| 9 | ModCellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Minimum Cell Voltage | Minimum voltage for all cells in this module.
| 10 | ModCellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with the minimum cell voltage.
| 11 | ModCellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average voltage for all cells in this module.
| 12 | ModAnoTmp |  |  | uint16 |  | Tmp_SF | C |  |  |  | Anolyte Temperature
| 13 | ModCatTmp |  |  | uint16 |  | Tmp_SF | C |  |  |  | Catholyte Temperature
| 14 | ModConSt |  |  | bitfield32 | [6 empty] | Contactor Status
|  | CONTACTOR_0 | 0
|  | CONTACTOR_1 | 1
|  | CONTACTOR_2 | 2
|  | CONTACTOR_3 | 3
|  | CONTACTOR_4 | 4
|  | CONTACTOR_5 | 5
|  | CONTACTOR_6 | 6
|  | CONTACTOR_7 | 7
|  | CONTACTOR_8 | 8
|  | CONTACTOR_9 | 9
|  | CONTACTOR_10 | 10
|  | CONTACTOR_11 | 11
|  | CONTACTOR_12 | 12
|  | CONTACTOR_13 | 13
|  | CONTACTOR_14 | 14
|  | CONTACTOR_15 | 15
|  | CONTACTOR_16 | 16
|  | CONTACTOR_17 | 17
|  | CONTACTOR_18 | 18
|  | CONTACTOR_19 | 19
|  | CONTACTOR_20 | 20
|  | CONTACTOR_21 | 21
|  | CONTACTOR_22 | 22
|  | CONTACTOR_23 | 23
|  | CONTACTOR_24 | 24
|  | CONTACTOR_25 | 25
|  | CONTACTOR_26 | 26
|  | CONTACTOR_27 | 27
|  | CONTACTOR_28 | 28
|  | CONTACTOR_29 | 29
|  | CONTACTOR_30 | 30
| 16 | ModEvt1 |  |  | bitfield32 |  |  |  |  | M |  | Module Event 1 | Alarms, warnings and status values. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | RESERVED_1 | 18
|  | RESERVED_2 | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | RESERVED_3 | 24
|  | RESERVED_4 | 25
|  | RESERVED_5 | 26
|  | FIRE_ALARM | 27
|  | MODULE_CONFIGURATION_ALARM | 28
|  | MODULE_CONFIGURATION_WARNING | 29
| 18 | ModEvt2 |  |  | bitfield32 |  |  |  |  | M |  | Module Event 2 | Alarms, warnings and status values. Bit flags.
|  | LEAK_ALARM | 0
|  | PUMP_ALARM | 1
|  | HIGH_PRESSURE_ALARM | 2
|  | HIGH_PRESSURE_WARNING | 3
|  | LOW_FLOW_ALARM | 4
|  | LOW_FLOW_WARNING | 5
| 20 | ModConFail |  |  | enum16 | [6 empty] | Connection Failure Reason
|  | NO_FAILURE | 0
|  | BUTTON_PUSHED | 1
|  | MODULE_GROUND_FAULT | 2
|  | OUTSIDE_VOLTAGE_RANGE | 3
|  | MODULE_NOT_ENABLED | 4
|  | FUSE_OPEN | 5
|  | CONTACTOR_FAILURE | 6
|  | PRECHARGE_FAILURE | 7
|  | MODULE_FAULT | 8
| 21 | ModSetEna |  |  | enum16 |  |  |  | RW |  |  | Enable/Disable Module | Enables and disables the module.
|  | ENABLE_MODULE | 1
|  | DISABLE_MODULE | 2
| 22 | ModSetCon |  |  | enum16 |  |  |  | RW |  |  | Connect/Disconnect Module | Connects and disconnects the module.
|  | CONNECT_MODULE | 1
|  | DISCONNECT_MODULE | 2
| 23 | ModDisRsn |  |  | enum16 | [6 empty] | Disabled Reason | Reason why the module is currently disabled.
|  | NONE | 0
|  | FAULT | 1
|  | MAINTENANCE | 2
|  | EXTERNAL | 3
|  | OTHER | 4

## 808 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | flow_battery_module |  |  | group | [6 empty] | Flow Battery Module Model
0 |  | ID | 808 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | ModuleTBD |  |  | uint16 |  |  |  |  | M |  | Module Points To Be Determined
|  | flow_battery_module.stack |  | 0 | group
| 0 | StackTBD |  |  | uint16 |  |  |  |  | M |  | Stack Points To Be Determined

## 809 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | flow_battery_stack |  |  | group | [6 empty] | Flow Battery Stack Model
0 |  | ID | 809 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | StackTBD |  |  | uint16 |  |  |  |  | M |  | Stack Points To Be Determined
|  | flow_battery_stack.cell |  | 0 | group
| 0 | CellTBD |  |  | uint16 |  |  |  |  | M |  | Cell Points To Be Determined

## 203 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | wye-connect three phase (abcn) meter
0 |  | ID | 203 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Amps | Total AC Current
3 |  | AphA |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseA | Phase A Current
4 |  | AphB |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseB | Phase B Current
5 |  | AphC |  |  | int16 |  | A_SF | A |  | M |  | Amps PhaseC | Phase C Current
6 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Current scale factor
7 |  | PhV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
8 |  | PhVphA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AN | Phase Voltage AN
9 |  | PhVphB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BN | Phase Voltage BN
10 |  | PhVphC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CN | Phase Voltage CN
11 |  | PPV |  |  | int16 |  | V_SF | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
12 |  | PhVphAB |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage AB | Phase Voltage AB
13 |  | PhVphBC |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage BC | Phase Voltage BC
14 |  | PhVphCA |  |  | int16 |  | V_SF | V |  | M |  | Phase Voltage CA | Phase Voltage CA
15 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Voltage scale factor
16 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  | M |  | Hz | Frequency
17 |  | Hz_SF |  |  | sunssf | [7 empty] | Frequency scale factor
18 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Watts | Total Real Power
19 |  | WphA |  |  | int16 |  | W_SF | W |  |  |  | Watts phase A
20 |  | WphB |  |  | int16 |  | W_SF | W |  |  |  | Watts phase B
21 |  | WphC |  |  | int16 |  | W_SF | W |  |  |  | Watts phase C
22 |  | W_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Power scale factor
23 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | VA | AC Apparent Power
24 |  | VAphA |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase A
25 |  | VAphB |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase B
26 |  | VAphC |  |  | int16 |  | VA_SF | VA |  |  |  | VA phase C
27 |  | VA_SF |  |  | sunssf | [7 empty] | Apparent Power scale factor
28 |  | VAR |  |  | int16 |  | VAR_SF | var |  |  |  | VAR | Reactive Power
29 |  | VARphA |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase A
30 |  | VARphB |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase B
31 |  | VARphC |  |  | int16 |  | VAR_SF | var |  |  |  | VAR phase C
32 |  | VAR_SF |  |  | sunssf | [7 empty] | Reactive Power scale factor
33 |  | PF |  |  | int16 |  | PF_SF | Pct |  |  |  | PF | Power Factor
34 |  | PFphA |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase A
35 |  | PFphB |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase B
36 |  | PFphC |  |  | int16 |  | PF_SF | Pct |  |  |  | PF phase C
37 |  | PF_SF |  |  | sunssf | [7 empty] | Power Factor scale factor
38 |  | TotWhExp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
40 |  | TotWhExpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase A
42 |  | TotWhExpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase B
44 |  | TotWhExpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Exported phase C
46 |  | TotWhImp |  |  | acc32 |  | TotWh_SF | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
48 |  | TotWhImpPhA |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase A
50 |  | TotWhImpPhB |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase B
52 |  | TotWhImpPhC |  |  | acc32 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Imported phase C
54 |  | TotWh_SF |  |  | sunssf |  |  |  |  | M |  |  | Real Energy scale factor
55 |  | TotVAhExp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
57 |  | TotVAhExpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase A
59 |  | TotVAhExpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase B
61 |  | TotVAhExpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Exported phase C
63 |  | TotVAhImp |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
65 |  | TotVAhImpPhA |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase A
67 |  | TotVAhImpPhB |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase B
69 |  | TotVAhImpPhC |  |  | acc32 |  | TotVAh_SF | VAh |  |  |  | Total VA-hours Imported phase C
71 |  | TotVAh_SF |  |  | sunssf | [7 empty] | Apparent Energy scale factor
72 |  | TotVArhImpQ1 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
74 |  | TotVArhImpQ1PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase A
76 |  | TotVArhImpQ1PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase B
78 |  | TotVArhImpQ1PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q1 phase C
80 |  | TotVArhImpQ2 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
82 |  | TotVArhImpQ2PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase A
84 |  | TotVArhImpQ2PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase B
86 |  | TotVArhImpQ2PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Imported Q2 phase C
88 |  | TotVArhExpQ3 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
90 |  | TotVArhExpQ3PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase A
92 |  | TotVArhExpQ3PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase B
94 |  | TotVArhExpQ3PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q3 phase C
96 |  | TotVArhExpQ4 |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
98 |  | TotVArhExpQ4PhA |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
100 |  | TotVArhExpQ4PhB |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
102 |  | TotVArhExpQ4PhC |  |  | acc32 |  | TotVArh_SF | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
104 |  | TotVArh_SF |  |  | sunssf | [7 empty] | Reactive Energy scale factor
105 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 213 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | ac_meter |  |  | group | [6 empty] | wye-connect three phase (abcn) meter
0 |  | ID | 213 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | A |  |  | float32 |  |  | A |  | M |  | Amps | Total AC Current
4 |  | AphA |  |  | float32 |  |  | A |  | M |  | Amps PhaseA | Phase A Current
6 |  | AphB |  |  | float32 |  |  | A |  | M |  | Amps PhaseB | Phase B Current
8 |  | AphC |  |  | float32 |  |  | A |  | M |  | Amps PhaseC | Phase C Current
10 |  | PhV |  |  | float32 |  |  | V |  | M |  | Voltage LN | Line to Neutral AC Voltage (average of active phases)
12 |  | PhVphA |  |  | float32 |  |  | V |  | M |  | Phase Voltage AN | Phase Voltage AN
14 |  | PhVphB |  |  | float32 |  |  | V |  | M |  | Phase Voltage BN | Phase Voltage BN
16 |  | PhVphC |  |  | float32 |  |  | V |  | M |  | Phase Voltage CN | Phase Voltage CN
18 |  | PPV |  |  | float32 |  |  | V |  | M |  | Voltage LL | Line to Line AC Voltage (average of active phases)
20 |  | PPVphAB |  |  | float32 |  |  | V |  | M |  | Phase Voltage AB | Phase Voltage AB
22 |  | PPVphBC |  |  | float32 |  |  | V |  | M |  | Phase Voltage BC | Phase Voltage BC
24 |  | PPVphCA |  |  | float32 |  |  | V |  | M |  | Phase Voltage CA | Phase Voltage CA
26 |  | Hz |  |  | float32 |  |  | Hz |  | M |  | Hz | Frequency
28 |  | W |  |  | float32 |  |  | W |  | M |  | Watts | Total Real Power
30 |  | WphA |  |  | float32 |  |  | W |  |  |  | Watts phase A
32 |  | WphB |  |  | float32 |  |  | W |  |  |  | Watts phase B
34 |  | WphC |  |  | float32 |  |  | W |  |  |  | Watts phase C
36 |  | VA |  |  | float32 |  |  | VA |  |  |  | VA | AC Apparent Power
38 |  | VAphA |  |  | float32 |  |  | VA |  |  |  | VA phase A
40 |  | VAphB |  |  | float32 |  |  | VA |  |  |  | VA phase B
42 |  | VAphC |  |  | float32 |  |  | VA |  |  |  | VA phase C
44 |  | VAR |  |  | float32 |  |  | var |  |  |  | VAR | Reactive Power
46 |  | VARphA |  |  | float32 |  |  | var |  |  |  | VAR phase A
48 |  | VARphB |  |  | float32 |  |  | var |  |  |  | VAR phase B
50 |  | VARphC |  |  | float32 |  |  | var |  |  |  | VAR phase C
52 |  | PF |  |  | float32 |  |  | PF |  |  |  | PF | Power Factor
54 |  | PFphA |  |  | float32 |  |  | PF |  |  |  | PF phase A
56 |  | PFphB |  |  | float32 |  |  | PF |  |  |  | PF phase B
58 |  | PFphC |  |  | float32 |  |  | PF |  |  |  | PF phase C
60 |  | TotWhExp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Exported | Total Real Energy Exported
62 |  | TotWhExpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase A
64 |  | TotWhExpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase B
66 |  | TotWhExpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Exported phase C
68 |  | TotWhImp |  |  | float32 |  |  | Wh |  | M |  | Total Watt-hours Imported | Total Real Energy Imported
70 |  | TotWhImpPhA |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase A
72 |  | TotWhImpPhB |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase B
74 |  | TotWhImpPhC |  |  | float32 |  |  | Wh |  |  |  | Total Watt-hours Imported phase C
76 |  | TotVAhExp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported | Total Apparent Energy Exported
78 |  | TotVAhExpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase A
80 |  | TotVAhExpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase B
82 |  | TotVAhExpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Exported phase C
84 |  | TotVAhImp |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported | Total Apparent Energy Imported
86 |  | TotVAhImpPhA |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase A
88 |  | TotVAhImpPhB |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase B
90 |  | TotVAhImpPhC |  |  | float32 |  |  | VAh |  |  |  | Total VA-hours Imported phase C
92 |  | TotVArhImpQ1 |  |  | float32 |  |  | varh |  |  |  | Total VAR-hours Imported Q1 | Total Reactive Energy Imported Quadrant 1
94 |  | TotVArhImpQ1phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase A
96 |  | TotVArhImpQ1phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase B
98 |  | TotVArhImpQ1phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q1 phase C
100 |  | TotVArhImpQ2 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 | Total Reactive Power Imported Quadrant 2
102 |  | TotVArhImpQ2phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase A
104 |  | TotVArhImpQ2phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase B
106 |  | TotVArhImpQ2phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Imported Q2 phase C
108 |  | TotVArhExpQ3 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 | Total Reactive Power Exported Quadrant 3
110 |  | TotVArhExpQ3phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase A
112 |  | TotVArhExpQ3phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase B
114 |  | TotVArhExpQ3phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q3 phase C
116 |  | TotVArhExpQ4 |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 | Total Reactive Power Exported Quadrant 4
118 |  | TotVArhExpQ4phA |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase A
120 |  | TotVArhExpQ4phB |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase B
122 |  | TotVArhExpQ4phC |  |  | float32 |  |  | varh |  |  |  | Total VAr-hours Exported Q4 Imported phase C
124 |  | Evt |  |  | bitfield32 |  |  |  |  | M |  | Events | Meter Event Flags
|  | M_EVENT_Power_Failure | 2
|  | M_EVENT_Under_Voltage | 3
|  | M_EVENT_Low_PF | 4
|  | M_EVENT_Over_Current | 5
|  | M_EVENT_Over_Voltage | 6
|  | M_EVENT_Missing_Sensor | 7
|  | M_EVENT_Reserved1 | 8
|  | M_EVENT_Reserved2 | 9
|  | M_EVENT_Reserved3 | 10
|  | M_EVENT_Reserved4 | 11
|  | M_EVENT_Reserved5 | 12
|  | M_EVENT_Reserved6 | 13
|  | M_EVENT_Reserved7 | 14
|  | M_EVENT_Reserved8 | 15
|  | M_EVENT_OEM01 | 16
|  | M_EVENT_OEM02 | 17
|  | M_EVENT_OEM03 | 18
|  | M_EVENT_OEM04 | 19
|  | M_EVENT_OEM05 | 20
|  | M_EVENT_OEM06 | 21
|  | M_EVENT_OEM07 | 22
|  | M_EVENT_OEM08 | 23
|  | M_EVENT_OEM09 | 24
|  | M_EVENT_OEM10 | 25
|  | M_EVENT_OEM11 | 26
|  | M_EVENT_OEM12 | 27
|  | M_EVENT_OEM13 | 28
|  | M_EVENT_OEM14 | 29
|  | M_EVENT_OEM15 | 30

## 63001 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_63001 |  |  | group | [6 empty] | SunSpec Test Model 1
0 |  | ID | 63001 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | sunssf_1 |  |  | sunssf
3 |  | sunssf_2 |  |  | sunssf
4 |  | sunssf_3 |  |  | sunssf
5 |  | sunssf_4 |  |  | sunssf
6 |  | int16_1 |  |  | int16 |  | sunssf_1
7 |  | int16_2 |  |  | int16 |  | sunssf_2
8 |  | int16_3 |  |  | int16 |  | sunssf_3
9 |  | int16_4 |  |  | int16 |  | sunssf_4 |  | RW
10 |  | int16_5 |  |  | int16
11 |  | int16_u |  |  | int16
12 |  | uint16_1 |  |  | uint16 |  | sunssf_1
13 |  | uint16_2 |  |  | uint16 |  | sunssf_2
14 |  | uint16_3 |  |  | uint16 |  | sunssf_3
15 |  | uint16_4 |  |  | uint16 |  | sunssf_4 |  | RW
16 |  | uint16_5 |  |  | uint16
17 |  | uint16_u |  |  | uint16
18 |  | acc16 |  |  | acc16
19 |  | acc16_u |  |  | acc16
20 |  | enum16 |  |  | enum16
21 |  | enum16_u |  |  | enum16
22 |  | bitfield16 |  |  | bitfield16
23 |  | bitfield16_u |  |  | bitfield16
24 |  | int32_1 |  |  | int32 |  | sunssf_5
26 |  | int32_2 |  |  | int32 |  | sunssf_6
28 |  | int32_3 |  |  | int32 |  | sunssf_7 |  | RW
30 |  | int32_4 |  |  | int32
32 |  | int32_5 |  |  | int32
34 |  | int32_u |  |  | int32
36 |  | uint32_1 |  |  | uint32 |  | sunssf_5
38 |  | uint32_2 |  |  | uint32 |  | sunssf_6
40 |  | uint32_3 |  |  | uint32 |  | sunssf_7 |  | RW
42 |  | uint32_4 |  |  | uint32 |  | 1
44 |  | uint32_5 |  |  | uint32
46 |  | uint32_u |  |  | uint32
48 |  | acc32 |  |  | acc32
50 |  | acc32_u |  |  | acc32
52 |  | enum32 |  |  | enum32
54 |  | enum32_u |  |  | enum32
56 |  | bitfield32 |  |  | bitfield32
58 |  | bitfield32_u |  |  | bitfield32
60 |  | ipaddr |  |  | ipaddr |  |  |  | RW
62 |  | ipaddr_u |  |  | ipaddr
64 |  | int64 |  |  | int64 |  |  |  | RW
68 |  | int64_u |  |  | int64
72 |  | acc64 |  |  | acc64
76 |  | acc64_u |  |  | acc64
80 |  | ipv6addr |  |  | ipv6addr
88 |  | ipv6addr_u |  |  | ipv6addr
96 |  | float32 |  |  | float32 |  |  |  | RW
98 |  | float32_u |  |  | float32
100 |  | string |  |  | string | 16 |  |  | RW
116 |  | string_u |  |  | string | 16
132 |  | sunssf_5 |  |  | sunssf
133 |  | sunssf_6 |  |  | sunssf
134 |  | sunssf_7 |  |  | sunssf
135 |  | pad_1 |  |  | pad
|  | model_63001.repeating |  | 0 | group
| 0 | sunssf_8 |  |  | sunssf
| 1 | int16_11 |  |  | int16 |  | sunssf_8 |  | RW
| 2 | int16_12 |  |  | int16 |  | sunssf_9
| 3 | int16_u |  |  | int16
| 4 | uint16_11 |  |  | uint16 |  | sunssf_8 |  | RW
| 5 | uint16_12 |  |  | uint16 |  | sunssf_9
| 6 | uint16_13 |  |  | uint16
| 7 | uint16_u |  |  | uint16
| 8 | int32 |  |  | int32 |  | sunssf_1 |  | RW
| 10 | int32_u |  |  | int32
| 12 | uint32 |  |  | uint32 |  | sunssf_9 |  | RW
| 14 | uint32_u |  |  | uint32
| 16 | sunssf_9 |  |  | sunssf
| 17 | pad_2 |  |  | pad

## 63002 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_63002 |  |  | group | [6 empty] | SunSpec Test Model 2
0 |  | ID | 63002 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
|  | model_63002.repeating |  | 0 | group
| 0 | sunssf_1 |  |  | sunssf
| 1 | int16_1 |  |  | int16 |  | sunssf_1 |  | RW
| 2 | int16_2 |  |  | int16 |  | sunssf_2
| 3 | sunssf_2 |  |  | sunssf

## 64001 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64001 |  |  | group | [6 empty] | Veris Status and Configuration
0 |  | ID | 64001 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Cmd |  |  | enum16 |  |  |  | RW |  |  | Command Code
3 |  | HWRev |  |  | uint16 | [6 empty] | Hardware Revision
4 |  | RSFWRev |  |  | uint16 | [6 empty] | RS FW Revision
5 |  | OSFWRev |  |  | uint16 | [6 empty] | OS FW Revision
6 |  | ProdRev |  |  | string | 2 | [5 empty] | Product Revision
8 |  | Boots |  |  | uint16 | [6 empty] | Boot Count
9 |  | Switch |  |  | bitfield16 | [6 empty] | DIP Switches
10 |  | Sensors |  |  | uint16 | [6 empty] | Num Detected Sensors
11 |  | Talking |  |  | uint16 | [6 empty] | Num Communicating Sensors
12 |  | Status |  |  | bitfield16 | [6 empty] | System Status
13 |  | Config |  |  | bitfield16 | [6 empty] | System Configuration
14 |  | LEDblink |  |  | uint16 |  |  | Pct |  |  |  | LED Blink Threshold
15 |  | LEDon |  |  | uint16 |  |  | Pct |  |  |  | LED On Threshold
16 |  | Reserved |  |  | uint16
17 |  | Loc |  |  | string | 16 | [5 empty] | Location String
33 |  | S1ID |  |  | enum16 | [6 empty] | Sensor 1 Unit ID
34 |  | S1Addr |  |  | uint16 | [6 empty] | Sensor 1 Address
35 |  | S1OSVer |  |  | uint16 | [6 empty] | Sensor 1 OS Version
36 |  | S1Ver |  |  | string | 2 | [5 empty] | Sensor 1 Product Version
38 |  | S1Serial |  |  | string | 5 | [5 empty] | Sensor 1 Serial Num
43 |  | S2ID |  |  | enum16 | [6 empty] | Sensor 2 Unit ID
44 |  | S2Addr |  |  | uint16 | [6 empty] | Sensor 2 Address
45 |  | S2OSVer |  |  | uint16 | [6 empty] | Sensor 2 OS Version
46 |  | S2Ver |  |  | string | 2 | [5 empty] | Sensor 2 Product Version
48 |  | S2Serial |  |  | string | 5 | [5 empty] | Sensor 2 Serial Num
53 |  | S3ID |  |  | enum16 | [6 empty] | Sensor 3 Unit ID
54 |  | S3Addr |  |  | uint16 | [6 empty] | Sensor 3 Address
55 |  | S3OSVer |  |  | uint16 | [6 empty] | Sensor 3 OS Version
56 |  | S3Ver |  |  | string | 2 | [5 empty] | Sensor 3 Product Version
58 |  | S3Serial |  |  | string | 5 | [5 empty] | Sensor 3 Serial Num
63 |  | S4ID |  |  | enum16 | [6 empty] | Sensor 4 Unit ID
64 |  | S4Addr |  |  | uint16 | [6 empty] | Sensor 4 Address
65 |  | S4OSVer |  |  | uint16 | [6 empty] | Sensor 4 OS Version
66 |  | S4Ver |  |  | string | 2 | [5 empty] | Sensor 4 Product Version
68 |  | S4Serial |  |  | string | 5 | [5 empty] | Sensor 4 Serial Num

## 64020 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64020 |  |  | group | [6 empty] | Mersen GreenString
0 |  | ID | 64020 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Aux0Tmp |  |  | int16 |  |  | C |  |  |  | Aux 0 temperature
3 |  | Aux1Tmp |  |  | int16 |  |  | C |  |  |  | Aux 1 temperature
4 |  | Aux2Tmp |  |  | int16 |  |  | C |  |  |  | Aux 2 temperature
5 |  | Aux3Tmp |  |  | int16 |  |  | C |  |  |  | Aux 3 temperature
6 |  | Aux4Tmp |  |  | int16 |  |  | C |  |  |  | Aux 4 temperature
7 |  | ProbeTmp |  |  | int16 |  |  | C |  | M |  | Probe Temperature
8 |  | MainTmp |  |  | int16 |  |  | C |  | M |  | Main Temperature
9 |  | SensorV_SF |  |  | sunssf |  |  |  |  | M |  | Voltage scale factor for the sensors
10 |  | SensorA_SF |  |  | sunssf |  |  |  |  | M |  | Current scale factor for the sensors
11 |  | SensorHz_SF |  |  | sunssf |  |  |  |  | M |  | Frequency scale factor for the sensors
12 |  | Sensor1Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor1 Voltage | scale of 0-10V
13 |  | Sensor2Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor2 Voltage | scale of 0-10V
14 |  | Sensor3Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor3 Voltage | scale of 0-10V
15 |  | Sensor4Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor4 Voltage | scale of 0-10V
16 |  | Sensor5Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor5 Voltage | scale of 0-10V
17 |  | Sensor6Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor6 Voltage | scale of 0-10V
18 |  | Sensor7Voltage |  |  | int16 |  | SensorV_SF | V |  |  |  | Sensor7 Voltage | scale of 0-10V
19 |  | Sensor1Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor1 Current | scale of 4-20mA
20 |  | Sensor2Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor2 Current | in 4-20mA or 4-20mA
21 |  | Sensor3Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor3 Current | in 4-20mA or 4-20mA
22 |  | Sensor4Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor4 Current | in 4-20mA or 4-20mA
23 |  | Sensor5Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor5 Current | in 4-20mA or 4-20mA
24 |  | Sensor6Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor6 Current | in 4-20mA or 4-20mA
25 |  | Sensor7Current |  |  | int16 |  | SensorA_SF | A |  |  |  | Sensor7 Current | in 4-20mA or 4-20mA
26 |  | Sensor8 |  |  | uint16 |  | SensorHz_SF | Hz |  |  |  | Sensor8 frequency | frequency in Hz
27 |  | Relay1 |  |  | uint16 | [6 empty] | Relay 1 state
28 |  | Relay2 |  |  | uint16 | [6 empty] | Relay 2 state
29 |  | Relay3 |  |  | uint16 | [6 empty] | Relay 3 state
30 |  | ResetAccumulators |  |  | uint16 | [6 empty] | Reset the accumulators | always 0 in reading, used the code 0xC0DA during the writing for resetting them
31 |  | Reset |  |  | uint16 | [6 empty] | Reset the system | always 0 in reading, used the code 0xC0DA during the writing for resetting the system
|  | model_64020.repeating |  | 0 | group
| 0 | SerialNumber |  |  | string | 9 |  |  |  | M |  | Serial number | strings of 16 characters
| 9 | Firmware |  |  | string | 6 |  |  |  | M |  | Firmware version | string of 11 characters
| 15 | Hardware |  |  | uint16 |  |  |  |  | M |  | Hardware version

## 64101 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64101 |  |  | group | [6 empty] | Eltek Inverter Extension
0 |  | ID | 64101 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Eltek_Country_Code |  |  | uint16
3 |  | Eltek_Feeding_Phase |  |  | uint16
4 |  | Eltek_APD_Method |  |  | uint16
5 |  | Eltek_APD_Power_Ref |  |  | uint16
6 |  | Eltek_RPS_Method |  |  | uint16
7 |  | Eltek_RPS_Q_Ref |  |  | uint16
8 |  | Eltek_RPS_CosPhi_Ref |  |  | int16

## 64110 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64110 |  |  | group | [6 empty] | OutBack AXS device
0 |  | ID | 64110 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | MajorFWRev |  |  | uint16 |  |  |  |  | M |  | AXS Major Firmware Number
3 |  | MidFWRev |  |  | uint16 |  |  |  |  | M |  | AXS Mid Firmware Number
4 |  | MinorFWRev |  |  | uint16 |  |  |  |  | M |  | AXS Minor Firmware Number
5 |  | EncrypKey |  |  | uint16 |  |  |  |  | M |  | Encryption Key
6 |  | MAC_Address |  |  | string | 7 |  |  |  | M |  | MAC Address
13 |  | WritePassword |  |  | string | 8 |  |  |  | M |  | Write Password
21 |  | EnableDHCP |  |  | enum16 |  |  |  |  | M |  | Enable DHCP
22 |  | TCPIP_address |  |  | ipaddr |  |  |  |  | M |  | TCPIP Address
24 |  | Gateway_address |  |  | ipaddr |  |  |  |  | M |  | TCPIP Gateway
26 |  | TCPIP_Netmask |  |  | ipaddr |  |  |  |  | M |  | TCPIP Netmask
28 |  | DNS1_address |  |  | ipaddr |  |  |  |  | M |  | TCPIP DNS1
30 |  | DNS2_address |  |  | ipaddr |  |  |  |  | M |  | TCPIP DNS2
32 |  | Modbus_port |  |  | uint16 |  |  |  |  | M |  | ModBus Port
33 |  | SMTP_server_nm |  |  | string | 20 |  |  |  | M |  | SMTP Server Name
53 |  | SMTP_account_nm |  |  | string | 16 |  |  |  | M |  | SMTP Account Name
69 |  | SMTP_enable_SSL |  |  | enum16 |  |  |  |  | M |  | Enable SMTP SSL
|  | ASX_DISABLED | 0
|  | ASX_ENABLED | 1
70 |  | SMTP_password |  |  | string | 8 |  |  |  | M |  | SMTP Password
78 |  | SMTP_user_nm |  |  | string | 20 |  |  |  | M |  | SMTP User Name
98 |  | Stat_email_int |  |  | uint16 |  |  |  |  | M |  | Status Email Interval
99 |  | Stat_start_HR |  |  | uint16 |  |  |  |  | M |  | Status Email Start Hour
100 |  | Stat_email_sub |  |  | string | 25 |  |  |  | M |  | Status Email Subject
125 |  | Stat_email_addr1 |  |  | string | 20 |  |  |  | M |  | Status Email to Address 1
145 |  | Stat_email_addr2 |  |  | string | 20 |  |  |  | M |  | Status Email to Address 2
165 |  | Alarm_email_en |  |  | enum16 |  |  |  |  | M |  | Enable Alarm Email
|  | ASX_DISABLED | 0
|  | ASX_ENABLED | 1
166 |  | Alarm_email_sub |  |  | string | 25 |  |  |  | M |  | Alarm Email Subject
191 |  | Alarm_email_addr1 |  |  | string | 20 |  |  |  | M |  | Alarm Email to Address 1
211 |  | Alarm_email_addr2 |  |  | string | 20 |  |  |  | M |  | Alarm Email to Address 2
231 |  | FTP_password |  |  | string | 8 |  |  |  | M |  | FTP Password
239 |  | TELNET_password |  |  | string | 8 |  |  |  | M |  | Telnet Password
247 |  | Log_write_int |  |  | uint16 |  |  | Tms |  | M |  | SD-Card Datalog Write Interval
248 |  | Log_retain |  |  | uint16 |  |  | Tmd |  | M |  | SD-Card Datalog Retain
249 |  | Log_mode |  |  | enum16 |  |  |  |  | M |  | SD-Card Datalog Mode
|  | LOG_DISABLED | 0
|  | LOG_EXCEL | 1
|  | LOG_COMPACT | 2
250 |  | NTP_server_nm |  |  | string | 20 |  |  |  | M |  | NTP Timer Server Name
270 |  | NTP_enable |  |  | enum16 |  |  |  |  | M |  | Enable Network Time
|  | ASX_DISABLED | 0
|  | ASX_ENABLED | 1
271 |  | TimeZone |  |  | int16 |  |  | Tmh |  | M |  | Time Zone
272 |  | Date_year |  |  | uint16 |  |  |  |  | M |  | Year
273 |  | Date_month |  |  | uint16 |  |  |  |  | M |  | Month
274 |  | Date_Day |  |  | uint16 |  |  |  |  | M |  | Day
275 |  | Time_hour |  |  | uint16 |  |  |  |  | M |  | Hour
276 |  | Time_minute |  |  | uint16 |  |  |  |  | M |  | Minute
277 |  | Time_second |  |  | uint16 |  |  |  |  | M |  | Second
278 |  | Battery_temp |  |  | int16 |  | Temp_SF | C |  | M |  | Battery Temperature
279 |  | Ambient_temp |  |  | int16 |  | Temp_SF | C |  | M |  | Ambient Temperature
280 |  | Temp_SF |  |  | sunssf |  |  |  |  | M
281 |  | AXS_Error |  |  | bitfield16 |  |  |  |  | M |  | AXS Error
282 |  | AXS_Status |  |  | bitfield16 |  |  |  |  | M |  | AXS Status
283 |  | AXS_Spare |  |  | uint16 |  |  |  |  | M |  | Spare

## 64111 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64111 |  |  | group | [6 empty] | Basic Charge Controller
0 |  | ID | 64111 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Port |  |  | uint16 |  |  |  |  | M |  | Port Number
3 |  | V_SF |  |  | sunssf |  |  |  |  | M
4 |  | A_SF |  |  | sunssf |  |  |  |  | M
5 |  | P_SF |  |  | sunssf |  |  |  |  | M
6 |  | AH_SF |  |  | sunssf |  |  |  |  | M
7 |  | KWH_SF |  |  | sunssf |  |  |  |  | M
8 |  | BattV |  |  | uint16 |  | V_SF | V |  | M |  | Battery Voltage
9 |  | ArrayV |  |  | uint16 |  | V_SF | V |  | M |  | Array Voltage
10 |  | OutputA |  |  | uint16 |  | A_SF | A |  | M |  | Output Current
11 |  | InputA |  |  | uint16 |  | P_SF | A |  | M |  | Array Current
12 |  | ChargerSt |  |  | enum16 |  |  |  |  | M |  | Operating State
|  | Off | 0
|  | Float | 1
|  | Bulk | 2
|  | Absorb | 3
|  | EQ | 4
13 |  | OutputW |  |  | uint16 |  | P_SF | W |  | M |  | Output Wattage
14 |  | TodayMinBatV |  |  | uint16 |  | V_SF | V |  | M |  | Today's Minimum Battery Voltage
15 |  | TodayMaxBatV |  |  | uint16 |  | V_SF | V |  | M |  | Today's Maximum Battery Voltage
16 |  | VOCV |  |  | uint16 |  | V_SF | V |  | M |  | VOC
17 |  | TodayMaxVOC |  |  | uint16 |  | V_SF | V |  | M |  | Today's Maximum VOC
18 |  | TodaykWhOutput |  |  | uint16 |  | KWH_SF | kWh |  | M |  | Today's kWh
19 |  | TodayAHOutput |  |  | uint16 |  | AH_SF | AH |  | M |  | Today's AH
20 |  | LifeTimeKWHOut |  |  | uint16 |  | P_SF | kWh |  | M |  | Lifetime kWh
21 |  | LifeTimeAHOut |  |  | uint16 |  | KWH_SF | kAH |  | M |  | Lifetime kAH
22 |  | LifeTimeMaxOut |  |  | uint16 |  | P_SF | W |  | M |  | Lifetime Maximum Output Wattage
23 |  | LifeTimeMaxBatt |  |  | uint16 |  | V_SF | V |  | M |  | Lifetime Maximum Battery Voltage
24 |  | LifeTimeMaxVOC |  |  | uint16 |  | V_SF | V |  | M |  | Lifetime Maximum VOC Voltage

## 64112 (hidden)
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description
|  | model_64112 |  |  | group | [6 empty] | OutBack FM Charge Controller
0 |  | ID | 64112 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | Port |  |  | uint16 |  |  |  |  | M |  | Port Number
3 |  | V_SF |  |  | sunssf |  |  |  |  | M
4 |  | C_SF |  |  | sunssf |  |  |  |  | M
5 |  | H_SF |  |  | sunssf |  |  |  |  | M
6 |  | P_SF |  |  | sunssf |  |  |  |  | M
7 |  | AH_SF |  |  | sunssf |  |  |  |  | M
8 |  | KWH_SF |  |  | sunssf |  |  |  |  | M
9 |  | CC_Config_fault |  |  | bitfield16 |  |  |  |  | M |  | Faults
10 |  | CC_Config_absorb_V |  |  | uint16 |  | V_SF | V |  | M |  | Absorb
11 |  | CC_Config_absorb_Hr |  |  | uint16 |  | H_SF | Tmh |  | M |  | Absorb Time
12 |  | CC_Config_absorb_End_A |  |  | uint16 |  | V_SF | A |  | M |  | Absorb End
13 |  | CC_Config_rebulk_V |  |  | uint16 |  | V_SF | V |  | M |  | Rebulk
14 |  | CC_Config_float_V |  |  | uint16 |  | V_SF | V |  | M |  | Float
15 |  | CC_Config_max_Chg_A |  |  | uint16 |  | V_SF | A |  | M |  | Maximum Charge
16 |  | CC_Config_equalize_V |  |  | uint16 |  | V_SF | V |  | M |  | Equalize
17 |  | CC_Config_equalize_Hr |  |  | uint16 |  |  | Tmh |  | M |  | Equalize Time
18 |  | CC_Config_auto_equalize |  |  | uint16 |  |  | Tmd |  | M |  | Auto Equalize Interval
19 |  | CC_Config_MPPT_mode |  |  | enum16 |  |  |  |  | M |  | MPPT mode
|  | Auto | 0
|  | U_Pick | 1
|  | Wind | 2
20 |  | CC_Config_sweep_width |  |  | enum16 |  |  |  |  | M |  | Sweep Width
|  | Half | 0
|  | Full | 1
21 |  | CC_Config_sweep_max |  |  | enum16 |  |  |  |  | M |  | Sweep Maximum
|  | Eighty_Percent | 0
|  | Eighty_Five_Percent | 1
|  | Ninty_Percent | 2
|  | Ninty_Nine_Percent | 3
22 |  | CC_Config_U_Pick_Duty_cyc |  |  | uint16 |  | V_SF | Pct |  | M |  | U-Pick PWM Duty Cycle
23 |  | CC_Config_grid_tie |  |  | enum16 |  |  |  |  | M |  | Grid Tie Mode
|  | Disabled | 0
|  | Enabled | 1
24 |  | CC_Config_temp_comp |  |  | enum16 |  |  |  |  | M |  | Temp Comp Mode
|  | Wide | 0
|  | Limited | 1
25 |  | CC_Config_temp_comp_llimt |  |  | uint16 |  | V_SF | V |  | M |  | Temp Comp Lower Limit
26 |  | CC_Config_temp_comp_hlimt |  |  | uint16 |  | V_SF | V |  | M |  | Temp Comp Upper Limit
27 |  | CC_Config_auto_restart |  |  | enum16 |  |  |  |  | M |  | Auto Restart Mode
|  | Off | 0
|  | Every_90_Minutes | 1
|  | Every_90_Minutes_if_Absorb_or_Float | 2
28 |  | CC_Config_wakeup_VOC |  |  | uint16 |  | V_SF | V |  | M |  | Wakeup VOC Change
29 |  | CC_Config_snooze_mode_A |  |  | uint16 |  | V_SF | A |  | M |  | Snooze Mode
30 |  | CC_Config_wakeup_interval |  |  | uint16 |  |  | Tms |  | M |  | Wakeup Interval
31 |  | CC_Config_AUX_mode |  |  | enum16 |  |  |  |  | M |  | AUX Output Mode
|  | Float | 0
|  | Diversion_Relay | 1
|  | Diversion_Solid_St | 2
|  | Low_Batt_Disconnect | 3
|  | Remote | 4
|  | Vent_Fan | 5
|  | PV_Trigger | 6
|  | Error_Output | 7
|  | Night_Light | 8
32 |  | CC_Config_AUX_control |  |  | enum16 |  |  |  |  | M |  | AUX Output Control
|  | Off | 0
|  | Auto | 1
|  | On | 2
33 |  | CC_Config_AUX_state |  |  | enum16 |  |  |  |  | M |  | AUX Output State
|  | Disabled | 0
|  | Enabled | 1
34 |  | CC_Config_AUX_polarity |  |  | enum16 |  |  |  |  | M |  | AUX Output Polarity
|  | Low | 0
|  | High | 1
35 |  | CC_Config_AUX_L_Batt_disc |  |  | uint16 |  | V_SF | V |  | M |  | AUX Low Battery Disconnect
36 |  | CC_Config_AUX_L_Batt_rcon |  |  | uint16 |  | V_SF | V |  | M |  | AUX Low Battery Reconnect
37 |  | CC_Config_AUX_L_Batt_dly |  |  | uint16 |  |  | Tms |  | M |  | AUX Low Battery Disconnect Delay
38 |  | CC_Config_AUX_Vent_fan_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Vent Fan
39 |  | CC_Config_AUX_PV_triggerV |  |  | uint16 |  | V_SF | V |  | M |  | AUX PV Trigger
40 |  | CC_Config_AUX_PV_trg_h_tm |  |  | uint16 |  |  | Tms |  | M |  | AUX PV Trigger Hold Time
41 |  | CC_Config_AUX_Nlite_ThrsV |  |  | uint16 |  | V_SF | V |  | M |  | AUX Night Light Threshold
42 |  | CC_Config_AUX_Nlite_On_tm |  |  | uint16 |  | H_SF | Tmh |  | M |  | AUX Night Light On Time
43 |  | CC_Config_AUX_Nlite_On_hist |  |  | uint16 |  |  | Tms |  | M |  | AUX Night Light On Hysteresis
44 |  | CC_Config_AUX_Nlite_Off_hist |  |  | uint16 |  |  | Tms |  | M |  | AUX Night Light Off Hysteresis
45 |  | CC_Config_AUX_Error_batt_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Error Output Low Battery
46 |  | CC_Config_AUX_Divert_h_time |  |  | uint16 |  | V_SF | Tms |  | M |  | AUX Divert Hold Time
47 |  | CC_Config_AUX_Divert_dly_time |  |  | uint16 |  |  | Tms |  | M |  | AUX Divert Delay Time
48 |  | CC_Config_AUX_Divert_Rel_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Divert Relative
49 |  | CC_Config_AUX_Divert_Hyst_V |  |  | uint16 |  | V_SF | V |  | M |  | AUX Divert Hysteresis
50 |  | CC_Config_MajorFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Major Firmware Number
51 |  | CC_Config_MidFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Mid Firmware Number
52 |  | CC_Config_MinorFWRev |  |  | uint16 |  |  |  |  | M |  | FM CC Minor Firmware Number
53 |  | CC_Config_DataLog_Day_offset |  |  | uint16 |  |  | Tmd |  | M |  | Set Data Log Day Offset
54 |  | CC_Config_DataLog_Cur_Day_off |  |  | uint16 |  |  | Tmd |  | M |  | Current Data Log Day Offset
55 |  | CC_Config_DataLog_Daily_AH |  |  | uint16 |  |  | Ah |  | M |  | Data Log Daily (Ah)
56 |  | CC_Config_DataLog_Daily_KWH |  |  | uint16 |  | KWH_SF | kWh |  | M |  | Data Log Daily (kWh)
57 |  | CC_Config_DataLog_Max_Out_A |  |  | uint16 |  | V_SF | A |  | M |  | Data Log Daily Maximum Output (A)
58 |  | CC_Config_DataLog_Max_Out_W |  |  | uint16 |  | V_SF | W |  | M |  | Data Log Daily Maximum Output (W)
59 |  | CC_Config_DataLog_Absorb_T |  |  | uint16 |  |  | Tms |  | M |  | Data Log Daily Absorb Time
60 |  | CC_Config_DataLog_Float_T |  |  | uint16 |  |  | Tms |  | M |  | Data Log Daily Float Time
61 |  | CC_Config_DataLog_Min_Batt_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Minimum Battery
62 |  | CC_Config_DataLog_Max_Batt_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Maximum Battery
63 |  | CC_Config_DataLog_Max_Input_V |  |  | uint16 |  | V_SF | V |  | M |  | Data Log Daily Maximum Input
64 |  | CC_Config_DataLog_Clear |  |  | uint16 |  |  |  |  | M |  | Data Log Clear
65 |  | CC_Config_DataLog_Clr_Comp |  |  | uint16 |  |  |  |  | M |  | Data Log Clear Complement